## Summary
A3 — Cable Schedule, Audit View
Project | Kingsford Hotel Bacolod — BMS Rehabilitation (A/B run)
Canonical source | A3-cable-schedule.yaml
How to record corrections | Edit the canonical YAML directly — add a verification: block to the affected row(s)
Totals
Total cables | 211
Total length (m) | 6,780
Field cables | 198
Trunk cables | 7
Panel power feeds | 6
Verification status
Status | Count | % of total
verified | 0 | 0%
needs_correction | 0 | 0%
uncertain | 0 | 0%
unverified | 211 | 100%
⚠ Known weak points
Cable lengths are estimates based on assumption A-001 (30 m average panel-to-device run, 80 m trunk per floor). Field-verified lengths typically vary by ±20% per cable. THIS IS THE SYSTEM'S WEAKEST AUTO-GENERATED QUANTITY — please verify before issuing the BOQ to the customer.
How corrections flow
1. Open A3-cable-schedule.yaml in any text editor.
2. Find the affected row by ID (column A in the Detail sheet).
3. Add a verification: block — see the 'Verification schema' sheet for the template.
4. Re-run: python3 _playbook/tools/generate-deliverables.py <project>
5. Corrections flow through B4 manhours, BOQ material costs, and final deliverables automatically.

## By Panel
Panel | Cable count | Total length (m)
FCP-2F | 68 | 2040
FCP-RD | 37 | 1110
MCP-PLANT | 28 | 840
FCP-3F | 27 | 810
FCP-BSMT | 20 | 600
FCP-GF | 18 | 540
TOTAL (field cables) | 198 | 5940

## By Floor
Floor | Cable count | Total length (m)
2nd Floor | 96 | 2880
Roofdeck | 37 | 1110
3rd Floor | 27 | 810
Ground | 18 | 540
Lower Ground | 14 | 420
Basement | 6 | 180
TOTAL | 198 | 5940

## By Cable Type
Cable type | Count | Total length (m)
4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 98 | 2940
4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 46 | 1380
4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 29 | 870
Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 23 | 690
Modbus shielded twisted-pair, 1pr × 22 AWG (e.g., Belden 9841) | 2 | 60

## Detail (cables)
ID | From | To | Cable type | Length (m) | Status | Corrected (m) | Verified by | Date | Drawing ref | Notes
C0001 | FCP-GF | AHU-1.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0002 | FCP-GF | AHU-1.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0003 | FCP-GF | AHU-1.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0004 | FCP-GF | AHU-1.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0005 | FCP-GF | AHU-1.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0006 | FCP-GF | AHU-1.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0007 | FCP-GF | AHU-1.3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0008 | FCP-GF | AHU-1.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0009 | FCP-GF | AHU-1.3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0010 | FCP-2F | AHU-2M.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0011 | FCP-2F | AHU-2M.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0012 | FCP-2F | AHU-2M.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0013 | FCP-2F | AHU-2M.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0014 | FCP-2F | AHU-2M.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0015 | FCP-2F | AHU-2M.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0016 | FCP-2F | AHU-B.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0017 | FCP-2F | AHU-B.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0018 | FCP-2F | AHU-B.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0019 | FCP-2F | AHU-B.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0020 | FCP-2F | AHU-B.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0021 | FCP-2F | AHU-B.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0022 | FCP-2F | AHU-B.3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0023 | FCP-2F | AHU-B.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0024 | FCP-2F | AHU-B.3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0025 | FCP-2F | AHU-EL (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0026 | FCP-2F | AHU-EL (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0027 | FCP-2F | AHU-EL (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0028 | FCP-2F | AHU-FR2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0029 | FCP-2F | AHU-FR2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0030 | FCP-2F | AHU-FR2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0031 | FCP-2F | AHU-FR3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0032 | FCP-2F | AHU-FR3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0033 | FCP-2F | AHU-FR3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0034 | FCP-2F | AHU-PF (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0035 | FCP-2F | AHU-PF (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0036 | FCP-2F | AHU-PF (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0037 | FCP-BSMT | ATS-1 (EE Contractor) | Modbus shielded twisted-pair, 1pr × 22 AWG (e.g., Belden 9841) | 30 | unverified
C0038 | FCP-BSMT | BLR-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0039 | FCP-BSMT | BLR-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0040 | FCP-BSMT | BLR-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0041 | FCP-BSMT | BLR-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0042 | MCP-PLANT | CH-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0043 | MCP-PLANT | CH-1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0044 | MCP-PLANT | CH-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0045 | MCP-PLANT | CH-2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0046 | MCP-PLANT | CH-3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0047 | MCP-PLANT | CH-3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0048 | MCP-PLANT | CHW-BYPASS (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0049 | MCP-PLANT | CHW-HDR-R (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0050 | MCP-PLANT | CHW-HDR-S (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0051 | FCP-RD | COW-HDR (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0052 | FCP-RD | CT-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0053 | FCP-RD | CT-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0054 | FCP-RD | CT-1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0055 | FCP-RD | CT-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0056 | FCP-RD | CT-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0057 | FCP-RD | CT-2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0058 | FCP-RD | CT-3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0059 | FCP-RD | CT-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0060 | FCP-RD | CT-3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0061 | FCP-RD | CT-COMMON (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0062 | FCP-2F | DOAS-2M (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0063 | FCP-2F | DOAS-2M (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0064 | FCP-2F | DOAS-2M (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0065 | FCP-RD | DOAS-RD.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0066 | FCP-RD | DOAS-RD.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0067 | FCP-RD | DOAS-RD.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0068 | FCP-RD | DOAS-RD.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0069 | FCP-RD | DOAS-RD.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0070 | FCP-RD | DOAS-RD.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0071 | FCP-GF | EF-1.2A (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0072 | FCP-GF | EF-1MR.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0073 | FCP-GF | EF-1ST0.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0074 | FCP-2F | EF-2.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0075 | FCP-2F | EF-2.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0076 | FCP-2F | EF-2.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0077 | FCP-2F | EF-2.4 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0078 | FCP-2F | EF-2B.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0079 | FCP-2F | EF-2B.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0080 | FCP-3F | EF-3GE.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0081 | FCP-3F | EF-3GE.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0082 | FCP-2F | EF-CHR.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0083 | FCP-2F | EF-CHR.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0084 | FCP-2F | EF-GS.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0085 | FCP-2F | EF-GS.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0086 | FCP-GF | EF-LPG.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0087 | FCP-GF | EF-MRF.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0088 | FCP-BSMT | GEN-1 (EE Contractor) | Modbus shielded twisted-pair, 1pr × 22 AWG (e.g., Belden 9841) | 30 | unverified
C0089 | FCP-RD | HP-HZ.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0090 | FCP-RD | HP-HZ.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0091 | FCP-RD | HP-HZ.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0092 | FCP-BSMT | HP-LZ.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0093 | FCP-BSMT | HP-LZ.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0094 | FCP-BSMT | HP-LZ.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0095 | FCP-RD | HW-HDR-HZ (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0096 | FCP-BSMT | HW-HDR-LZ (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0097 | FCP-RD | HWT-HZ.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0098 | FCP-RD | HWT-HZ.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0099 | FCP-RD | HWT-HZ.3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0100 | FCP-BSMT | HWT-LZ.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0101 | FCP-BSMT | HWT-LZ.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0102 | FCP-BSMT | HWT-LZ.3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0103 | FCP-2F | ION-2M.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0104 | FCP-2F | ION-2M.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0105 | FCP-2F | ION-2M.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0106 | FCP-2F | ION-2M.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0107 | FCP-BSMT | PAHU-0.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0108 | FCP-BSMT | PAHU-0.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0109 | FCP-BSMT | PAHU-0.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0110 | FCP-2F | PAHU-B1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0111 | FCP-2F | PAHU-B1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0112 | FCP-2F | PAHU-B1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0113 | FCP-2F | PAHU-B2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0114 | FCP-2F | PAHU-B2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0115 | FCP-2F | PAHU-B2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0116 | FCP-2F | PAHU-B3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0117 | FCP-2F | PAHU-B3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0118 | FCP-2F | PAHU-B3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0119 | FCP-2F | PAHU-FR (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0120 | FCP-2F | PAHU-FR (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0121 | FCP-2F | PAHU-FR (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0122 | FCP-2F | PAHU-PF (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0123 | FCP-2F | PAHU-PF (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0124 | FCP-2F | PAHU-PF (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0125 | FCP-RD | PAHU-RD.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0126 | FCP-RD | PAHU-RD.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0127 | FCP-RD | PAHU-RD.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0128 | FCP-RD | PAHU-RD.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0129 | FCP-RD | PAHU-RD.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0130 | FCP-RD | PAHU-RD.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0131 | MCP-PLANT | PCHW-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0132 | MCP-PLANT | PCHW-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0133 | MCP-PLANT | PCHW-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0134 | MCP-PLANT | PCHW-S (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0135 | MCP-PLANT | PCOW-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0136 | MCP-PLANT | PCOW-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0137 | MCP-PLANT | PCOW-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0138 | FCP-RD | RP-HZ.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0139 | FCP-RD | RP-HZ.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0140 | FCP-RD | RP-HZ.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0141 | FCP-BSMT | RP-LZ.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0142 | FCP-BSMT | RP-LZ.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0143 | FCP-BSMT | RP-LZ.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0144 | FCP-GF | TEF-1.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0145 | FCP-GF | TEF-1.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0146 | FCP-GF | TEF-1.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0147 | FCP-GF | TEF-1.4 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0148 | FCP-2F | TEF-2.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0149 | FCP-2F | TEF-2.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0150 | FCP-2F | TEF-2B.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0151 | FCP-3F | TEF-3A.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0152 | FCP-3F | TEF-3A.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0153 | FCP-3F | TEF-3B.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0154 | FCP-3F | TEF-3C.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0155 | FCP-3F | TEF-3C.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0156 | FCP-3F | TEF-3D.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0157 | FCP-3F | TEF-3D.10 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0158 | FCP-3F | TEF-3D.11 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0159 | FCP-3F | TEF-3D.12 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0160 | FCP-3F | TEF-3D.13 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0161 | FCP-3F | TEF-3D.14 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0162 | FCP-3F | TEF-3D.15 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0163 | FCP-3F | TEF-3D.16 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0164 | FCP-3F | TEF-3D.17 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0165 | FCP-3F | TEF-3D.18 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0166 | FCP-3F | TEF-3D.19 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0167 | FCP-3F | TEF-3D.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0168 | FCP-3F | TEF-3D.20 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0169 | FCP-3F | TEF-3D.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0170 | FCP-3F | TEF-3D.4 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0171 | FCP-3F | TEF-3D.5 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0172 | FCP-3F | TEF-3D.6 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0173 | FCP-3F | TEF-3D.7 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0174 | FCP-3F | TEF-3D.8 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0175 | FCP-3F | TEF-3D.9 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0176 | FCP-BSMT | PAHU-0.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0177 | FCP-2F | PAHU-B1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0178 | FCP-2F | PAHU-B2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0179 | FCP-2F | PAHU-B3 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0180 | FCP-2F | PAHU-PF (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0181 | FCP-2F | PAHU-FR (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0182 | FCP-2F | DOAS-2M (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0183 | FCP-RD | DOAS-RD.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0184 | FCP-RD | DOAS-RD.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0185 | FCP-RD | PAHU-RD.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0186 | FCP-RD | PAHU-RD.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0187 | MCP-PLANT | CH-1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0188 | MCP-PLANT | CH-2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0189 | MCP-PLANT | CH-3 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0190 | MCP-PLANT | PM-MAIN (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0191 | MCP-PLANT | PM-GEN (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0192 | MCP-PLANT | PM-MCC-CHILLER (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0193 | MCP-PLANT | PM-MCC-CT (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0194 | MCP-PLANT | PM-MCC-BOILER (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0195 | MCP-PLANT | PM-MCC-FIRE-PUMP (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0196 | MCP-PLANT | PM-MCC-MDP-1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0197 | MCP-PLANT | PM-MCC-MDP-2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0198 | MCP-PLANT | PM-MCC-MDP-3 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
T0199 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0200 | BMS Server Room (head-end) | All BMS panels at 3rd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0201 | BMS Server Room (head-end) | All BMS panels at Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0202 | BMS Server Room (head-end) | All BMS panels at Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0203 | BMS Server Room (head-end) | All BMS panels at Lower Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0204 | BMS Server Room (head-end) | All BMS panels at Roofdeck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0205 | BMS Server Room (head-end) | All BMS panel controllers (MS/TP daisy-chain or branched) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 180 | unverified
P0206 | Local panelboard / EE-supplied feeder | FCP-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0207 | Local panelboard / EE-supplied feeder | FCP-3F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0208 | Local panelboard / EE-supplied feeder | FCP-BSMT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0209 | Local panelboard / EE-supplied feeder | FCP-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0210 | Local panelboard / EE-supplied feeder | FCP-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0211 | Local panelboard / EE-supplied feeder | MCP-PLANT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified

## Verification schema
How to record verification / corrections in A3-cable-schedule.yaml
Find the affected row in the YAML by ID (Detail sheet column A) and add a verification: block:
- id: C0001
from: PNL-CH-PLANT-GND
to: CH-1 (BMS Contractor)
cable_type: 4C × 1.5 mm² shielded FRLS
length_m: 30
verification: # ADDED by team
status: needs_correction # unverified ¦ verified ¦ needs_correction ¦ uncertain
corrected_length_m: 42 # team's measured / confirmed value
verified_by: J. Cruz
verified_date: 2026-05-10
drawing_ref: "EE-09 grid B-2"
notes: ""
After saving, re-run: python3 _playbook/tools/generate-deliverables.py <project>
Corrections propagate to B4 manhours, BOQ, and final deliverables automatically.
Recommended verification methods (priority order):
1. Site walkthrough with measurement (most accurate; for cable lengths, after structural completion).
2. Properly-scaled architectural drawings.
3. Mechanical contractor's tray layout combined with BMS panel locations.
4. A-001 default with ±20% contingency in BOQ — last resort.