## Summary
A1 — Consolidated I/O List Summary
Project | Kingsford Hotel Bacolod — BMS Rehabilitation (A/B run)
Total I/O rows | 762
By type
DI | 381
AI | 184
HLI | 110
AO | 64
Network | 23
By C/O
Equipment Supplier | 469
BMS Contractor | 206
ME Contractor | 82
EE Contractor | 5
By system
VENT | 366
AC | 334
HWL | 48
EE | 14
By panel
FCP-2F | 272
MCP-PLANT | 136
FCP-RD | 129
FCP-3F | 81
FCP-BSMT | 75
FCP-GF | 69

## All IO Points
ID | System | Equipment Class | Equipment Instance | Location | Point Description | Type | Field Device | C/O | DoO Ref | Panel | Source | Notes
P0001 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Indoor Return Air Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0002 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Indoor Return Air Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0003 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0004 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0005 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0006 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0007 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0008 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0009 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0010 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0011 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0012 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0013 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0014 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0015 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Indoor Return Air Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0016 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Indoor Return Air Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0017 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0018 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0019 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0020 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0021 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0022 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0023 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0024 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0025 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0026 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0027 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0028 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0029 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Indoor Return Air Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0030 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Indoor Return Air Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0031 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0032 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0033 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0034 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0035 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0036 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0037 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0038 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0039 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0040 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0041 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0042 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0043 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Indoor Return Air Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0044 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Indoor Return Air Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0045 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0046 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0047 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0048 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0049 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0050 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0051 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0052 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0053 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0054 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0055 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0056 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0057 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Indoor Return Air Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0058 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Indoor Return Air Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0059 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0060 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0061 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0062 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0063 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0064 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0065 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0066 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0067 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0068 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0069 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0070 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0071 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Indoor Return Air Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0072 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Indoor Return Air Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0073 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0074 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0075 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0076 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0077 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0078 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0079 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0080 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0081 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0082 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0083 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0084 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0085 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Indoor Return Air Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0086 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Indoor Return Air Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0087 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0088 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0089 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0090 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0091 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0092 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0093 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0094 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0095 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0096 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0097 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0098 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0099 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Indoor Return Air Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0100 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Indoor Return Air Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0101 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0102 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0103 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0104 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0105 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0106 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0107 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0108 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0109 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0110 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0111 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0112 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0113 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Indoor Return Air Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0114 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Indoor Return Air Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0115 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0116 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0117 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0118 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0119 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0120 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0121 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0122 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0123 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0124 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0125 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0126 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0127 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Indoor Return Air Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0128 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Indoor Return Air Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0129 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0130 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0131 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0132 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0133 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0134 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0135 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0136 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0137 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0138 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0139 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0140 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Chilled-Water-Served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0141 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0142 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Outside Supply Air Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0143 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0144 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0145 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0146 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0147 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0148 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0149 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0150 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0151 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0152 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0153 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0154 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | BACnet/IP drop | Network | RJ45 to edge switch | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0155 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0156 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | Outside Supply Air Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0157 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0158 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0159 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0160 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0161 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0162 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0163 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0164 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0165 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0166 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0167 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0168 | VENT | Precooled Air Handling Unit | PAHU-B1 | 2nd Floor | BACnet/IP drop | Network | RJ45 to edge switch | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0169 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0170 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | Outside Supply Air Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0171 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0172 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0173 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0174 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0175 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0176 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0177 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0178 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0179 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0180 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0181 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0182 | VENT | Precooled Air Handling Unit | PAHU-B2 | 2nd Floor | BACnet/IP drop | Network | RJ45 to edge switch | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0183 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0184 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | Outside Supply Air Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0185 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0186 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0187 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0188 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0189 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0190 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0191 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0192 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0193 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0194 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0195 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0196 | VENT | Precooled Air Handling Unit | PAHU-B3 | 2nd Floor | BACnet/IP drop | Network | RJ45 to edge switch | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0197 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0198 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | Outside Supply Air Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0199 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0200 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0201 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0202 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0203 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0204 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0205 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0206 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0207 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0208 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0209 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0210 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Floor | BACnet/IP drop | Network | RJ45 to edge switch | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0211 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0212 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | Outside Supply Air Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0213 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0214 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0215 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0216 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0217 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0218 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0219 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0220 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0221 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0222 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0223 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0224 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Floor | BACnet/IP drop | Network | RJ45 to edge switch | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0225 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Indoor Return Air Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0226 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Indoor Return Air Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0227 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0228 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0229 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0230 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0231 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0232 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0233 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0234 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0235 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0236 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0237 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0238 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0239 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Outdoor Air Humidity (Casino) | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0240 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Indoor Mixed Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0241 | AC | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor (Casino) | Return Air CO sensor (Casino) | AI | CO Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0242 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Indoor Return Air Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0243 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Indoor Return Air Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0244 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0245 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0246 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0247 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0248 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0249 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0250 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0251 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0252 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0253 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0254 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0255 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0256 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Outdoor Air Humidity (Casino) | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0257 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Indoor Mixed Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0258 | AC | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor (Casino) | Return Air CO sensor (Casino) | AI | CO Sensor | BMS Contractor | DRC-004-2024 AC/AHU (Modulating CHW-served) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0259 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0260 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Outside Supply Air Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0261 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0262 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Outdoor Supply Air Motorized Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0263 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Outdoor Supply Air Motorized Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0264 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Recovery Wheel Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0265 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Recovery Wheel Motor Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0266 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Supply Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0267 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Supply Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0268 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Supply Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0269 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Supply Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0270 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Supply Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0271 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Indoor Mixed Air Temperature | AI | Temperature Sensor | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0272 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Indoor Mixed Air Humidity | AI | Humidity Sensor | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0273 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | CHWS Cooling Coil Valve Status | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0274 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0275 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0276 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Indoor Exhaust Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0277 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Indoor Exhaust Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0278 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Exhaust Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0279 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Exhaust Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0280 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Exhaust Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0281 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Exhaust Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0282 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | Exhaust Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0283 | VENT | DOAS Unit | DOAS-2M | 2nd Floor (Casino) | BACnet/IP drop | Network | RJ45 to edge switch | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0284 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0285 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Outside Supply Air Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0286 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0287 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Outdoor Supply Air Motorized Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0288 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Outdoor Supply Air Motorized Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0289 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Recovery Wheel Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0290 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Recovery Wheel Motor Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0291 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Supply Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0292 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Supply Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0293 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Supply Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0294 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Supply Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0295 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Supply Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0296 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Indoor Mixed Air Temperature | AI | Temperature Sensor | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0297 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Indoor Mixed Air Humidity | AI | Humidity Sensor | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0298 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | CHWS Cooling Coil Valve Status | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0299 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0300 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0301 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Indoor Exhaust Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0302 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Indoor Exhaust Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0303 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Exhaust Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0304 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Exhaust Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0305 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Exhaust Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0306 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Exhaust Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0307 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | Exhaust Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0308 | VENT | DOAS Unit | DOAS-RD.1 | Roofdeck | BACnet/IP drop | Network | RJ45 to edge switch | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0309 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0310 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Outside Supply Air Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0311 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0312 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Outdoor Supply Air Motorized Damper Status | DI | Damper Controller | ME Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0313 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Outdoor Supply Air Motorized Damper Control | AO | Damper Controller | ME Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0314 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Recovery Wheel Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0315 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Recovery Wheel Motor Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0316 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Supply Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0317 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Supply Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0318 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Supply Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0319 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Supply Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0320 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Supply Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0321 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Indoor Mixed Air Temperature | AI | Temperature Sensor | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0322 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Indoor Mixed Air Humidity | AI | Humidity Sensor | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0323 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | CHWS Cooling Coil Valve Status | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0324 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0325 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0326 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Indoor Exhaust Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0327 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Indoor Exhaust Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0328 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Exhaust Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0329 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Exhaust Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0330 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Exhaust Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0331 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Exhaust Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0332 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | Exhaust Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0333 | VENT | DOAS Unit | DOAS-RD.2 | Roofdeck | BACnet/IP drop | Network | RJ45 to edge switch | BMS Contractor | DRC-004-2024 VENT/DOAS Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0334 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0335 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | Outside Supply Air Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0336 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0337 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0338 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0339 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0340 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0341 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0342 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0343 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0344 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0345 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0346 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0347 | VENT | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck | BACnet/IP drop | Network | RJ45 to edge switch | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0348 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | Outside Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0349 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | Outside Supply Air Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0350 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0351 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | Outdoor Damper Status | DI | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0352 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | Outdoor Damper Control | AO | Damper Controller | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0353 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0354 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | CHWS Valve Control | AO | Electric Valve Actuator | ME Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0355 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0356 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0357 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0358 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | Fan VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0359 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | Fan Control | HLI | VFD | Equipment Supplier | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0360 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0361 | VENT | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck | BACnet/IP drop | Network | RJ45 to edge switch | BMS Contractor | DRC-004-2024 VENT/Precooled Air Handling Unit | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0362 | AC | Ozone Generator (UV-light or Corona) | ION-2M.1 | 2nd Floor (Casino) | Equipment Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Ozone Generator (UV-light or Corona) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0363 | AC | Ozone Generator (UV-light or Corona) | ION-2M.1 | 2nd Floor (Casino) | Equipment Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Ozone Generator (UV-light or Corona) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0364 | AC | Ozone Generator (UV-light or Corona) | ION-2M.1 | 2nd Floor (Casino) | VOC Monitoring | AI | VOC Sensor | BMS Contractor | DRC-004-2024 AC/Ozone Generator (UV-light or Corona) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0365 | AC | Ozone Generator (UV-light or Corona) | ION-2M.2 | 2nd Floor (Casino) | Equipment Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Ozone Generator (UV-light or Corona) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0366 | AC | Ozone Generator (UV-light or Corona) | ION-2M.2 | 2nd Floor (Casino) | Equipment Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Ozone Generator (UV-light or Corona) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0367 | AC | Ozone Generator (UV-light or Corona) | ION-2M.2 | 2nd Floor (Casino) | VOC Monitoring | AI | VOC Sensor | BMS Contractor | DRC-004-2024 AC/Ozone Generator (UV-light or Corona) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0368 | VENT | Exhaust Fan (Toilet) | TEF-1.1 | Ground Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0369 | VENT | Exhaust Fan (Toilet) | TEF-1.1 | Ground Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0370 | VENT | Exhaust Fan (Toilet) | TEF-1.1 | Ground Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0371 | VENT | Exhaust Fan (Toilet) | TEF-1.2 | Ground Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0372 | VENT | Exhaust Fan (Toilet) | TEF-1.2 | Ground Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0373 | VENT | Exhaust Fan (Toilet) | TEF-1.2 | Ground Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0374 | VENT | Exhaust Fan (Toilet) | TEF-1.3 | Ground Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0375 | VENT | Exhaust Fan (Toilet) | TEF-1.3 | Ground Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0376 | VENT | Exhaust Fan (Toilet) | TEF-1.3 | Ground Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0377 | VENT | Exhaust Fan (Toilet) | TEF-1.4 | Ground Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0378 | VENT | Exhaust Fan (Toilet) | TEF-1.4 | Ground Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0379 | VENT | Exhaust Fan (Toilet) | TEF-1.4 | Ground Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0380 | VENT | Exhaust Fan (General) | EF-1.2A | Ground Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0381 | VENT | Exhaust Fan (General) | EF-1.2A | Ground Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0382 | VENT | Exhaust Fan (General) | EF-1.2A | Ground Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0383 | VENT | Exhaust Fan (General) | EF-LPG.1 | Ground Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0384 | VENT | Exhaust Fan (General) | EF-LPG.1 | Ground Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0385 | VENT | Exhaust Fan (General) | EF-LPG.1 | Ground Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0386 | VENT | Exhaust Fan (General) | EF-1MR.1 | Ground Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0387 | VENT | Exhaust Fan (General) | EF-1MR.1 | Ground Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0388 | VENT | Exhaust Fan (General) | EF-1MR.1 | Ground Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0389 | VENT | Exhaust Fan (General) | EF-1ST0.1 | Ground Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0390 | VENT | Exhaust Fan (General) | EF-1ST0.1 | Ground Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0391 | VENT | Exhaust Fan (General) | EF-1ST0.1 | Ground Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0392 | VENT | Exhaust Fan (General) | EF-MRF.1 | Ground Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0393 | VENT | Exhaust Fan (General) | EF-MRF.1 | Ground Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0394 | VENT | Exhaust Fan (General) | EF-MRF.1 | Ground Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-GF | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0395 | VENT | Exhaust Fan (Toilet) | TEF-2.1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0396 | VENT | Exhaust Fan (Toilet) | TEF-2.1 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0397 | VENT | Exhaust Fan (Toilet) | TEF-2.1 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0398 | VENT | Exhaust Fan (Toilet) | TEF-2.3 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0399 | VENT | Exhaust Fan (Toilet) | TEF-2.3 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0400 | VENT | Exhaust Fan (Toilet) | TEF-2.3 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0401 | VENT | Exhaust Fan (Toilet) | TEF-2B.3 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0402 | VENT | Exhaust Fan (Toilet) | TEF-2B.3 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0403 | VENT | Exhaust Fan (Toilet) | TEF-2B.3 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0404 | VENT | Exhaust Fan (General) | EF-2B.1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0405 | VENT | Exhaust Fan (General) | EF-2B.1 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0406 | VENT | Exhaust Fan (General) | EF-2B.1 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0407 | VENT | Exhaust Fan (General) | EF-2B.2 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0408 | VENT | Exhaust Fan (General) | EF-2B.2 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0409 | VENT | Exhaust Fan (General) | EF-2B.2 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0410 | VENT | Exhaust Fan (General) | EF-GS.1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0411 | VENT | Exhaust Fan (General) | EF-GS.1 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0412 | VENT | Exhaust Fan (General) | EF-GS.1 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0413 | VENT | Exhaust Fan (General) | EF-GS.2 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0414 | VENT | Exhaust Fan (General) | EF-GS.2 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0415 | VENT | Exhaust Fan (General) | EF-GS.2 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0416 | VENT | Exhaust Fan (General) | EF-2.1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0417 | VENT | Exhaust Fan (General) | EF-2.1 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0418 | VENT | Exhaust Fan (General) | EF-2.1 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0419 | VENT | Exhaust Fan (General) | EF-2.2 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0420 | VENT | Exhaust Fan (General) | EF-2.2 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0421 | VENT | Exhaust Fan (General) | EF-2.2 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0422 | VENT | Exhaust Fan (General) | EF-2.3 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0423 | VENT | Exhaust Fan (General) | EF-2.3 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0424 | VENT | Exhaust Fan (General) | EF-2.3 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0425 | VENT | Exhaust Fan (General) | EF-2.4 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0426 | VENT | Exhaust Fan (General) | EF-2.4 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0427 | VENT | Exhaust Fan (General) | EF-2.4 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0428 | VENT | Exhaust Fan (General) | EF-CHR.1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0429 | VENT | Exhaust Fan (General) | EF-CHR.1 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0430 | VENT | Exhaust Fan (General) | EF-CHR.1 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0431 | VENT | Exhaust Fan (General) | EF-CHR.2 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0432 | VENT | Exhaust Fan (General) | EF-CHR.2 | 2nd Floor | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0433 | VENT | Exhaust Fan (General) | EF-CHR.2 | 2nd Floor | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-2F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0434 | VENT | Exhaust Fan (Toilet) | TEF-3A.1 | 3rd Floor (Amenity) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0435 | VENT | Exhaust Fan (Toilet) | TEF-3A.1 | 3rd Floor (Amenity) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0436 | VENT | Exhaust Fan (Toilet) | TEF-3A.1 | 3rd Floor (Amenity) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0437 | VENT | Exhaust Fan (Toilet) | TEF-3A.2 | 3rd Floor (Amenity) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0438 | VENT | Exhaust Fan (Toilet) | TEF-3A.2 | 3rd Floor (Amenity) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0439 | VENT | Exhaust Fan (Toilet) | TEF-3A.2 | 3rd Floor (Amenity) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0440 | VENT | Exhaust Fan (Toilet) | TEF-3B.1 | 3rd Floor (Amenity) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0441 | VENT | Exhaust Fan (Toilet) | TEF-3B.1 | 3rd Floor (Amenity) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0442 | VENT | Exhaust Fan (Toilet) | TEF-3B.1 | 3rd Floor (Amenity) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0443 | VENT | Exhaust Fan (Toilet) | TEF-3C.1 | 3rd Floor (Amenity) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0444 | VENT | Exhaust Fan (Toilet) | TEF-3C.1 | 3rd Floor (Amenity) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0445 | VENT | Exhaust Fan (Toilet) | TEF-3C.1 | 3rd Floor (Amenity) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0446 | VENT | Exhaust Fan (Toilet) | TEF-3C.2 | 3rd Floor (Amenity) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0447 | VENT | Exhaust Fan (Toilet) | TEF-3C.2 | 3rd Floor (Amenity) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0448 | VENT | Exhaust Fan (Toilet) | TEF-3C.2 | 3rd Floor (Amenity) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0449 | VENT | Exhaust Fan (Toilet) | TEF-3D.1 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0450 | VENT | Exhaust Fan (Toilet) | TEF-3D.1 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0451 | VENT | Exhaust Fan (Toilet) | TEF-3D.1 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0452 | VENT | Exhaust Fan (Toilet) | TEF-3D.2 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0453 | VENT | Exhaust Fan (Toilet) | TEF-3D.2 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0454 | VENT | Exhaust Fan (Toilet) | TEF-3D.2 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0455 | VENT | Exhaust Fan (Toilet) | TEF-3D.3 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0456 | VENT | Exhaust Fan (Toilet) | TEF-3D.3 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0457 | VENT | Exhaust Fan (Toilet) | TEF-3D.3 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0458 | VENT | Exhaust Fan (Toilet) | TEF-3D.4 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0459 | VENT | Exhaust Fan (Toilet) | TEF-3D.4 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0460 | VENT | Exhaust Fan (Toilet) | TEF-3D.4 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0461 | VENT | Exhaust Fan (Toilet) | TEF-3D.5 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0462 | VENT | Exhaust Fan (Toilet) | TEF-3D.5 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0463 | VENT | Exhaust Fan (Toilet) | TEF-3D.5 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0464 | VENT | Exhaust Fan (Toilet) | TEF-3D.6 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0465 | VENT | Exhaust Fan (Toilet) | TEF-3D.6 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0466 | VENT | Exhaust Fan (Toilet) | TEF-3D.6 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0467 | VENT | Exhaust Fan (Toilet) | TEF-3D.7 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0468 | VENT | Exhaust Fan (Toilet) | TEF-3D.7 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0469 | VENT | Exhaust Fan (Toilet) | TEF-3D.7 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0470 | VENT | Exhaust Fan (Toilet) | TEF-3D.8 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0471 | VENT | Exhaust Fan (Toilet) | TEF-3D.8 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0472 | VENT | Exhaust Fan (Toilet) | TEF-3D.8 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0473 | VENT | Exhaust Fan (Toilet) | TEF-3D.9 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0474 | VENT | Exhaust Fan (Toilet) | TEF-3D.9 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0475 | VENT | Exhaust Fan (Toilet) | TEF-3D.9 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0476 | VENT | Exhaust Fan (Toilet) | TEF-3D.10 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0477 | VENT | Exhaust Fan (Toilet) | TEF-3D.10 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0478 | VENT | Exhaust Fan (Toilet) | TEF-3D.10 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0479 | VENT | Exhaust Fan (Toilet) | TEF-3D.11 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0480 | VENT | Exhaust Fan (Toilet) | TEF-3D.11 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0481 | VENT | Exhaust Fan (Toilet) | TEF-3D.11 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0482 | VENT | Exhaust Fan (Toilet) | TEF-3D.12 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0483 | VENT | Exhaust Fan (Toilet) | TEF-3D.12 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0484 | VENT | Exhaust Fan (Toilet) | TEF-3D.12 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0485 | VENT | Exhaust Fan (Toilet) | TEF-3D.13 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0486 | VENT | Exhaust Fan (Toilet) | TEF-3D.13 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0487 | VENT | Exhaust Fan (Toilet) | TEF-3D.13 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0488 | VENT | Exhaust Fan (Toilet) | TEF-3D.14 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0489 | VENT | Exhaust Fan (Toilet) | TEF-3D.14 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0490 | VENT | Exhaust Fan (Toilet) | TEF-3D.14 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0491 | VENT | Exhaust Fan (Toilet) | TEF-3D.15 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0492 | VENT | Exhaust Fan (Toilet) | TEF-3D.15 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0493 | VENT | Exhaust Fan (Toilet) | TEF-3D.15 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0494 | VENT | Exhaust Fan (Toilet) | TEF-3D.16 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0495 | VENT | Exhaust Fan (Toilet) | TEF-3D.16 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0496 | VENT | Exhaust Fan (Toilet) | TEF-3D.16 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0497 | VENT | Exhaust Fan (Toilet) | TEF-3D.17 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0498 | VENT | Exhaust Fan (Toilet) | TEF-3D.17 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0499 | VENT | Exhaust Fan (Toilet) | TEF-3D.17 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0500 | VENT | Exhaust Fan (Toilet) | TEF-3D.18 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0501 | VENT | Exhaust Fan (Toilet) | TEF-3D.18 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0502 | VENT | Exhaust Fan (Toilet) | TEF-3D.18 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0503 | VENT | Exhaust Fan (Toilet) | TEF-3D.19 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0504 | VENT | Exhaust Fan (Toilet) | TEF-3D.19 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0505 | VENT | Exhaust Fan (Toilet) | TEF-3D.19 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0506 | VENT | Exhaust Fan (Toilet) | TEF-3D.20 | 3rd Floor (Guestroom) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0507 | VENT | Exhaust Fan (Toilet) | TEF-3D.20 | 3rd Floor (Guestroom) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0508 | VENT | Exhaust Fan (Toilet) | TEF-3D.20 | 3rd Floor (Guestroom) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (Toilet) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0509 | VENT | Exhaust Fan (General) | EF-3GE.1 | 3rd Floor (Amenity) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0510 | VENT | Exhaust Fan (General) | EF-3GE.1 | 3rd Floor (Amenity) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0511 | VENT | Exhaust Fan (General) | EF-3GE.1 | 3rd Floor (Amenity) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0512 | VENT | Exhaust Fan (General) | EF-3GE.2 | 3rd Floor (Amenity) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0513 | VENT | Exhaust Fan (General) | EF-3GE.2 | 3rd Floor (Amenity) | Fan HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0514 | VENT | Exhaust Fan (General) | EF-3GE.2 | 3rd Floor (Amenity) | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Exhaust Fan (General) | FCP-3F | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0515 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Entering Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0516 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Leaving Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0517 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | CHW Isolation Valve Status (Return) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0518 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | CHW Isolation Valve Status (Supply) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0519 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Evaporator Approach dT | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0520 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Evaporator Approach dP | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0521 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Evaporator Refrigerant Pressure | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0522 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Evaporator Refrigerant Temperature | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0523 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Oil Sump Pressure | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0524 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Oil Sump Temperature | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0525 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Oil Pump Status | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0526 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Oil Pump Trip | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0527 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Compressor Status | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0528 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Compressor HOA Status | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0529 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Compressor Trip | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0530 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Motor Load Current | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0531 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Motor kW / BTU Meter | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0532 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Winding Temperature | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0533 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Condenser Refrigerant Pressure | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0534 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Condenser Refrigerant Temperature | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0535 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Condenser Approach dT | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0536 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Condenser Approach dP | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0537 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | COW Isolation Valve Status (Return) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0538 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | COW Isolation Valve Status (Supply) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0539 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Entering Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0540 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | Leaving Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0541 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | CHW Return Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0542 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | CHW Supply Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0543 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | COW Supply Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0544 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Floor (Plant Room) | BACnet/IP gateway | Network | Chiller native BACnet | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0545 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Entering Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0546 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Leaving Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0547 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | CHW Isolation Valve Status (Return) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0548 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | CHW Isolation Valve Status (Supply) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0549 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Evaporator Approach dT | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0550 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Evaporator Approach dP | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0551 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Evaporator Refrigerant Pressure | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0552 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Evaporator Refrigerant Temperature | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0553 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Oil Sump Pressure | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0554 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Oil Sump Temperature | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0555 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Oil Pump Status | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0556 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Oil Pump Trip | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0557 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Compressor Status | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0558 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Compressor HOA Status | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0559 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Compressor Trip | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0560 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Motor Load Current | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0561 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Motor kW / BTU Meter | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0562 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Winding Temperature | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0563 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Condenser Refrigerant Pressure | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0564 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Condenser Refrigerant Temperature | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0565 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Condenser Approach dT | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0566 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Condenser Approach dP | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0567 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | COW Isolation Valve Status (Return) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0568 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | COW Isolation Valve Status (Supply) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0569 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Entering Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0570 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | Leaving Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0571 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | CHW Return Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0572 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | CHW Supply Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0573 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | COW Supply Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0574 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Floor (Plant Room) | BACnet/IP gateway | Network | Chiller native BACnet | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0575 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Entering Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0576 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Leaving Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0577 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | CHW Isolation Valve Status (Return) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0578 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | CHW Isolation Valve Status (Supply) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0579 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Evaporator Approach dT | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0580 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Evaporator Approach dP | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0581 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Evaporator Refrigerant Pressure | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0582 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Evaporator Refrigerant Temperature | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0583 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Oil Sump Pressure | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0584 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Oil Sump Temperature | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0585 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Oil Pump Status | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0586 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Oil Pump Trip | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0587 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Compressor Status | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0588 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Compressor HOA Status | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0589 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Compressor Trip | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0590 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Motor Load Current | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0591 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Motor kW / BTU Meter | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0592 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Winding Temperature | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0593 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Condenser Refrigerant Pressure | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0594 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Condenser Refrigerant Temperature | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0595 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Condenser Approach dT | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0596 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Condenser Approach dP | HLI | Chiller Native | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0597 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | COW Isolation Valve Status (Return) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0598 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | COW Isolation Valve Status (Supply) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0599 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Entering Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0600 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | Leaving Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0601 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | CHW Return Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0602 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | CHW Supply Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0603 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | COW Supply Flow | AI | Flow Sensor | BMS Contractor | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0604 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Floor (Plant Room) | BACnet/IP gateway | Network | Chiller native BACnet | Equipment Supplier | DRC-004-2024 AC/Chiller (Package Water-Cooled) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0605 | AC | Primary CHW Pump | PCHW-1 | 2nd Floor (Plant Room) | CHW Supply Pressure | AI | Pressure Sensor | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0606 | AC | Primary CHW Pump | PCHW-1 | 2nd Floor (Plant Room) | On/Off Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0607 | AC | Primary CHW Pump | PCHW-1 | 2nd Floor (Plant Room) | HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0608 | AC | Primary CHW Pump | PCHW-1 | 2nd Floor (Plant Room) | VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0609 | AC | Primary CHW Pump | PCHW-1 | 2nd Floor (Plant Room) | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0610 | AC | Primary CHW Pump | PCHW-2 | 2nd Floor (Plant Room) | CHW Supply Pressure | AI | Pressure Sensor | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0611 | AC | Primary CHW Pump | PCHW-2 | 2nd Floor (Plant Room) | On/Off Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0612 | AC | Primary CHW Pump | PCHW-2 | 2nd Floor (Plant Room) | HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0613 | AC | Primary CHW Pump | PCHW-2 | 2nd Floor (Plant Room) | VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0614 | AC | Primary CHW Pump | PCHW-2 | 2nd Floor (Plant Room) | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0615 | AC | Primary CHW Pump | PCHW-3 | 2nd Floor (Plant Room) | CHW Supply Pressure | AI | Pressure Sensor | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0616 | AC | Primary CHW Pump | PCHW-3 | 2nd Floor (Plant Room) | On/Off Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0617 | AC | Primary CHW Pump | PCHW-3 | 2nd Floor (Plant Room) | HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0618 | AC | Primary CHW Pump | PCHW-3 | 2nd Floor (Plant Room) | VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0619 | AC | Primary CHW Pump | PCHW-3 | 2nd Floor (Plant Room) | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0620 | AC | Primary CHW Pump (Standby) | PCHW-S | 2nd Floor (Plant Room) | CHW Supply Pressure | AI | Pressure Sensor | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump (Standby) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0621 | AC | Primary CHW Pump (Standby) | PCHW-S | 2nd Floor (Plant Room) | On/Off Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump (Standby) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0622 | AC | Primary CHW Pump (Standby) | PCHW-S | 2nd Floor (Plant Room) | HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump (Standby) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0623 | AC | Primary CHW Pump (Standby) | PCHW-S | 2nd Floor (Plant Room) | VFD Speed | HLI | VFD | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump (Standby) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0624 | AC | Primary CHW Pump (Standby) | PCHW-S | 2nd Floor (Plant Room) | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Primary CHW Pump (Standby) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0625 | AC | Condenser Water Pump | PCOW-1 | 2nd Floor (Plant Room) | On/Off Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Condenser Water Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0626 | AC | Condenser Water Pump | PCOW-1 | 2nd Floor (Plant Room) | HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Condenser Water Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0627 | AC | Condenser Water Pump | PCOW-1 | 2nd Floor (Plant Room) | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Condenser Water Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0628 | AC | Condenser Water Pump | PCOW-2 | 2nd Floor (Plant Room) | On/Off Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Condenser Water Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0629 | AC | Condenser Water Pump | PCOW-2 | 2nd Floor (Plant Room) | HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Condenser Water Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0630 | AC | Condenser Water Pump | PCOW-2 | 2nd Floor (Plant Room) | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Condenser Water Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0631 | AC | Condenser Water Pump | PCOW-3 | 2nd Floor (Plant Room) | On/Off Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Condenser Water Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0632 | AC | Condenser Water Pump | PCOW-3 | 2nd Floor (Plant Room) | HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Condenser Water Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0633 | AC | Condenser Water Pump | PCOW-3 | 2nd Floor (Plant Room) | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Condenser Water Pump | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0634 | AC | Cooling Tower | CT-1 | Roofdeck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0635 | AC | Cooling Tower | CT-1 | Roofdeck | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0636 | AC | Cooling Tower | CT-1 | Roofdeck | Basin Low Level | DI | Level Sensor | BMS Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0637 | AC | Cooling Tower | CT-1 | Roofdeck | Basin High Level | DI | Level Sensor | BMS Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0638 | AC | Cooling Tower | CT-1 | Roofdeck | COW Isolation Valve Status (Return) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0639 | AC | Cooling Tower | CT-1 | Roofdeck | Blowdown Corrosion/Scale (pH) | AI | pH/Cond Sensor | ME Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0640 | AC | Cooling Tower | CT-1 | Roofdeck | Blowdown Valve Control | AO | Electric Valve Actuator | BMS Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0641 | AC | Cooling Tower | CT-2 | Roofdeck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0642 | AC | Cooling Tower | CT-2 | Roofdeck | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0643 | AC | Cooling Tower | CT-2 | Roofdeck | Basin Low Level | DI | Level Sensor | BMS Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0644 | AC | Cooling Tower | CT-2 | Roofdeck | Basin High Level | DI | Level Sensor | BMS Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0645 | AC | Cooling Tower | CT-2 | Roofdeck | COW Isolation Valve Status (Return) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0646 | AC | Cooling Tower | CT-2 | Roofdeck | Blowdown Corrosion/Scale (pH) | AI | pH/Cond Sensor | ME Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0647 | AC | Cooling Tower | CT-2 | Roofdeck | Blowdown Valve Control | AO | Electric Valve Actuator | BMS Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0648 | AC | Cooling Tower | CT-3 | Roofdeck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0649 | AC | Cooling Tower | CT-3 | Roofdeck | Fan Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0650 | AC | Cooling Tower | CT-3 | Roofdeck | Basin Low Level | DI | Level Sensor | BMS Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0651 | AC | Cooling Tower | CT-3 | Roofdeck | Basin High Level | DI | Level Sensor | BMS Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0652 | AC | Cooling Tower | CT-3 | Roofdeck | COW Isolation Valve Status (Return) | DI | Electric Valve Actuator | ME Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0653 | AC | Cooling Tower | CT-3 | Roofdeck | Blowdown Corrosion/Scale (pH) | AI | pH/Cond Sensor | ME Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0654 | AC | Cooling Tower | CT-3 | Roofdeck | Blowdown Valve Control | AO | Electric Valve Actuator | BMS Contractor | DRC-004-2024 AC/Cooling Tower | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0655 | AC | Cooling Tower (Common) | CT-COMMON | Roofdeck | Outside Air Temperature (CT area) | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Cooling Tower (Common) | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0656 | AC | Cooling Tower (Common) | CT-COMMON | Roofdeck | Outside Air Humidity (CT area) | AI | Humidity Sensor | BMS Contractor | DRC-004-2024 AC/Cooling Tower (Common) | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0657 | AC | Cooling Tower (Common) | CT-COMMON | Roofdeck | Condenser Return Header Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Cooling Tower (Common) | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0658 | AC | Cooling Tower (Common) | CT-COMMON | Roofdeck | Condenser Supply Header Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Cooling Tower (Common) | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0659 | AC | CHW Supply Main Header | CHW-HDR-S | 2nd Floor (Plant Room) | CHW Supply Header Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/CHW Supply Main Header | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0660 | AC | CHW Supply Main Header | CHW-HDR-S | 2nd Floor (Plant Room) | CHW Supply Header Pressure | AI | Pressure Sensor | BMS Contractor | DRC-004-2024 AC/CHW Supply Main Header | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0661 | AC | CHW Return Main Header | CHW-HDR-R | 2nd Floor (Plant Room) | CHW Return Header Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/CHW Return Main Header | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0662 | AC | CHW Return Main Header | CHW-HDR-R | 2nd Floor (Plant Room) | CHW Return Header Pressure | AI | Pressure Sensor | BMS Contractor | DRC-004-2024 AC/CHW Return Main Header | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0663 | AC | CHW Bypass Header | CHW-BYPASS | 2nd Floor (Plant Room) | Differential Pressure | AI | Diff. Pressure Sensor | BMS Contractor | DRC-004-2024 AC/CHW Bypass Header | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0664 | AC | CHW Bypass Header | CHW-BYPASS | 2nd Floor (Plant Room) | Differential Temperature | AI | Diff. Temp Sensor | BMS Contractor | DRC-004-2024 AC/CHW Bypass Header | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0665 | AC | CHW Bypass Header | CHW-BYPASS | 2nd Floor (Plant Room) | CHW Bypass Valve Status | DI | Electric Valve Actuator | BMS Contractor | DRC-004-2024 AC/CHW Bypass Header | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0666 | AC | CHW Bypass Header | CHW-BYPASS | 2nd Floor (Plant Room) | CHW Bypass Valve Control | AO | Electric Valve Actuator | BMS Contractor | DRC-004-2024 AC/CHW Bypass Header | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0667 | AC | Condenser Water Header | COW-HDR | Roofdeck | Condenser Supply Header Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Condenser Water Header | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0668 | AC | Condenser Water Header | COW-HDR | Roofdeck | Condenser Return Header Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 AC/Condenser Water Header | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0669 | VENT | Steam Boiler | BLR-1 | Lower Ground | Supply Steam Pressure | AI | Pressure Sensor | BMS Contractor | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0670 | VENT | Steam Boiler | BLR-1 | Lower Ground | Low Water Level | DI | Level Sensor | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0671 | VENT | Steam Boiler | BLR-1 | Lower Ground | High Water Level | DI | Level Sensor | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0672 | VENT | Steam Boiler | BLR-1 | Lower Ground | Burner Power | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0673 | VENT | Steam Boiler | BLR-1 | Lower Ground | Small Fire Control | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0674 | VENT | Steam Boiler | BLR-1 | Lower Ground | Big Fire Control | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0675 | VENT | Steam Boiler | BLR-1 | Lower Ground | Feedwater Pump Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0676 | VENT | Steam Boiler | BLR-1 | Lower Ground | Burner Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0677 | VENT | Steam Boiler | BLR-1 | Lower Ground | Burner Fire Running | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0678 | VENT | Steam Boiler | BLR-1 | Lower Ground | Blower Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0679 | VENT | Steam Boiler | BLR-1 | Lower Ground | Fuel Oil Pump Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0680 | VENT | Steam Boiler | BLR-1 | Lower Ground | Blowdown Valve Status | DI | Electric Valve Actuator | BMS Contractor | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0681 | VENT | Steam Boiler | BLR-1 | Lower Ground | Blowdown Valve Control | AO | Electric Valve Actuator | BMS Contractor | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0682 | VENT | Steam Boiler | BLR-1 | Lower Ground | Feedwater Supply Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0683 | VENT | Steam Boiler | BLR-1 | Lower Ground | Fluegas Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0684 | VENT | Steam Boiler | BLR-1 | Lower Ground | Fluegas Oxygen Level | AI | Oxygen Sensor | BMS Contractor | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0685 | VENT | Steam Boiler | BLR-2 | Lower Ground | Supply Steam Pressure | AI | Pressure Sensor | BMS Contractor | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0686 | VENT | Steam Boiler | BLR-2 | Lower Ground | Low Water Level | DI | Level Sensor | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0687 | VENT | Steam Boiler | BLR-2 | Lower Ground | High Water Level | DI | Level Sensor | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0688 | VENT | Steam Boiler | BLR-2 | Lower Ground | Burner Power | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0689 | VENT | Steam Boiler | BLR-2 | Lower Ground | Small Fire Control | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0690 | VENT | Steam Boiler | BLR-2 | Lower Ground | Big Fire Control | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0691 | VENT | Steam Boiler | BLR-2 | Lower Ground | Feedwater Pump Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0692 | VENT | Steam Boiler | BLR-2 | Lower Ground | Burner Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0693 | VENT | Steam Boiler | BLR-2 | Lower Ground | Burner Fire Running | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0694 | VENT | Steam Boiler | BLR-2 | Lower Ground | Blower Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0695 | VENT | Steam Boiler | BLR-2 | Lower Ground | Fuel Oil Pump Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0696 | VENT | Steam Boiler | BLR-2 | Lower Ground | Blowdown Valve Status | DI | Electric Valve Actuator | BMS Contractor | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0697 | VENT | Steam Boiler | BLR-2 | Lower Ground | Blowdown Valve Control | AO | Electric Valve Actuator | BMS Contractor | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0698 | VENT | Steam Boiler | BLR-2 | Lower Ground | Feedwater Supply Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0699 | VENT | Steam Boiler | BLR-2 | Lower Ground | Fluegas Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0700 | VENT | Steam Boiler | BLR-2 | Lower Ground | Fluegas Oxygen Level | AI | Oxygen Sensor | BMS Contractor | DRC-004-2024 VENT/Steam Boiler | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0701 | HWL | Calorifier (Hot Water Storage Tank) | HWT-LZ.1 | Lower Ground | Tank Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 HWL/Calorifier (Hot Water Storage Tank) | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0702 | HWL | Calorifier (Hot Water Storage Tank) | HWT-LZ.2 | Lower Ground | Tank Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 HWL/Calorifier (Hot Water Storage Tank) | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0703 | HWL | Calorifier (Hot Water Storage Tank) | HWT-LZ.3 | Lower Ground | Tank Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 HWL/Calorifier (Hot Water Storage Tank) | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0704 | HWL | Calorifier (Hot Water Storage Tank) | HWT-HZ.1 | Roofdeck | Tank Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 HWL/Calorifier (Hot Water Storage Tank) | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0705 | HWL | Calorifier (Hot Water Storage Tank) | HWT-HZ.2 | Roofdeck | Tank Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 HWL/Calorifier (Hot Water Storage Tank) | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0706 | HWL | Calorifier (Hot Water Storage Tank) | HWT-HZ.3 | Roofdeck | Tank Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 HWL/Calorifier (Hot Water Storage Tank) | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0707 | HWL | Hot Water Header Set | HW-HDR-LZ | Lower Ground | Hot Water Supply Header Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 HWL/Hot Water Header Set | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0708 | HWL | Hot Water Header Set | HW-HDR-LZ | Lower Ground | Hot Water Return Header Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 HWL/Hot Water Header Set | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0709 | HWL | Hot Water Header Set | HW-HDR-LZ | Lower Ground | Make-Up Cold Water Header Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 HWL/Hot Water Header Set | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0710 | HWL | Hot Water Header Set | HW-HDR-HZ | Roofdeck | Hot Water Supply Header Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 HWL/Hot Water Header Set | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0711 | HWL | Hot Water Header Set | HW-HDR-HZ | Roofdeck | Hot Water Return Header Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 HWL/Hot Water Header Set | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0712 | HWL | Hot Water Header Set | HW-HDR-HZ | Roofdeck | Make-Up Cold Water Header Temperature | AI | Temperature Sensor | BMS Contractor | DRC-004-2024 HWL/Hot Water Header Set | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0713 | HWL | Heat Pump | HP-LZ.1 | Lower Ground | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0714 | HWL | Heat Pump | HP-LZ.1 | Lower Ground | Pump HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0715 | HWL | Heat Pump | HP-LZ.1 | Lower Ground | Pump Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0716 | HWL | Heat Pump | HP-LZ.2 | Lower Ground | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0717 | HWL | Heat Pump | HP-LZ.2 | Lower Ground | Pump HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0718 | HWL | Heat Pump | HP-LZ.2 | Lower Ground | Pump Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0719 | HWL | Heat Pump | HP-LZ.3 | Lower Ground | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0720 | HWL | Heat Pump | HP-LZ.3 | Lower Ground | Pump HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0721 | HWL | Heat Pump | HP-LZ.3 | Lower Ground | Pump Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0722 | HWL | Heat Pump | HP-HZ.1 | Roofdeck | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0723 | HWL | Heat Pump | HP-HZ.1 | Roofdeck | Pump HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0724 | HWL | Heat Pump | HP-HZ.1 | Roofdeck | Pump Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0725 | HWL | Heat Pump | HP-HZ.2 | Roofdeck | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0726 | HWL | Heat Pump | HP-HZ.2 | Roofdeck | Pump HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0727 | HWL | Heat Pump | HP-HZ.2 | Roofdeck | Pump Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0728 | HWL | Heat Pump | HP-HZ.3 | Roofdeck | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0729 | HWL | Heat Pump | HP-HZ.3 | Roofdeck | Pump HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0730 | HWL | Heat Pump | HP-HZ.3 | Roofdeck | Pump Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Heat Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0731 | HWL | Recirculating Pump | RP-LZ.1 | Lower Ground | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0732 | HWL | Recirculating Pump | RP-LZ.1 | Lower Ground | Pump HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0733 | HWL | Recirculating Pump | RP-LZ.1 | Lower Ground | Pump Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0734 | HWL | Recirculating Pump | RP-LZ.2 | Lower Ground | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0735 | HWL | Recirculating Pump | RP-LZ.2 | Lower Ground | Pump HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0736 | HWL | Recirculating Pump | RP-LZ.2 | Lower Ground | Pump Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0737 | HWL | Recirculating Pump | RP-LZ.3 | Lower Ground | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0738 | HWL | Recirculating Pump | RP-LZ.3 | Lower Ground | Pump HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0739 | HWL | Recirculating Pump | RP-LZ.3 | Lower Ground | Pump Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0740 | HWL | Recirculating Pump | RP-HZ.1 | Roofdeck | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0741 | HWL | Recirculating Pump | RP-HZ.1 | Roofdeck | Pump HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0742 | HWL | Recirculating Pump | RP-HZ.1 | Roofdeck | Pump Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0743 | HWL | Recirculating Pump | RP-HZ.2 | Roofdeck | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0744 | HWL | Recirculating Pump | RP-HZ.2 | Roofdeck | Pump HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0745 | HWL | Recirculating Pump | RP-HZ.2 | Roofdeck | Pump Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0746 | HWL | Recirculating Pump | RP-HZ.3 | Roofdeck | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0747 | HWL | Recirculating Pump | RP-HZ.3 | Roofdeck | Pump HOA Status | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0748 | HWL | Recirculating Pump | RP-HZ.3 | Roofdeck | Pump Trip | DI | Auxiliary Contact | Equipment Supplier | DRC-004-2024 HWL/Recirculating Pump | FCP-RD | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0749 | EE | Multifunction Power Meter (Main) | PM-MAIN | 2nd Floor (Plant Room) | Multifunction Power Meter (Modbus) | Network | Modbus RTU meter | BMS Contractor | DRC-004-2024 EE/Multifunction Power Meter (Main) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0750 | EE | Multifunction Power Meter (Main) | PM-GEN | 2nd Floor (Plant Room) | Multifunction Power Meter (Modbus) | Network | Modbus RTU meter | BMS Contractor | DRC-004-2024 EE/Multifunction Power Meter (Main) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0751 | EE | Multifunction Power Meter (Feeder) | PM-MCC-CHILLER | 2nd Floor (Plant Room) | Multifunction Power Meter (Modbus) | Network | Modbus RTU meter | BMS Contractor | DRC-004-2024 EE/Multifunction Power Meter (Feeder) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0752 | EE | Multifunction Power Meter (Feeder) | PM-MCC-CT | 2nd Floor (Plant Room) | Multifunction Power Meter (Modbus) | Network | Modbus RTU meter | BMS Contractor | DRC-004-2024 EE/Multifunction Power Meter (Feeder) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0753 | EE | Multifunction Power Meter (Feeder) | PM-MCC-BOILER | 2nd Floor (Plant Room) | Multifunction Power Meter (Modbus) | Network | Modbus RTU meter | BMS Contractor | DRC-004-2024 EE/Multifunction Power Meter (Feeder) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0754 | EE | Multifunction Power Meter (Feeder) | PM-MCC-FIRE-PUMP | 2nd Floor (Plant Room) | Multifunction Power Meter (Modbus) | Network | Modbus RTU meter | BMS Contractor | DRC-004-2024 EE/Multifunction Power Meter (Feeder) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0755 | EE | Multifunction Power Meter (Feeder) | PM-MCC-MDP-1 | 2nd Floor (Plant Room) | Multifunction Power Meter (Modbus) | Network | Modbus RTU meter | BMS Contractor | DRC-004-2024 EE/Multifunction Power Meter (Feeder) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0756 | EE | Multifunction Power Meter (Feeder) | PM-MCC-MDP-2 | 2nd Floor (Plant Room) | Multifunction Power Meter (Modbus) | Network | Modbus RTU meter | BMS Contractor | DRC-004-2024 EE/Multifunction Power Meter (Feeder) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0757 | EE | Multifunction Power Meter (Feeder) | PM-MCC-MDP-3 | 2nd Floor (Plant Room) | Multifunction Power Meter (Modbus) | Network | Modbus RTU meter | BMS Contractor | DRC-004-2024 EE/Multifunction Power Meter (Feeder) | MCP-PLANT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0758 | EE | Multifunction Power Meter (Main) | GEN-1 | Basement (Genset) | Generator Run Status | DI | Auxiliary Contact | EE Contractor | DRC-004-2024 EE/Multifunction Power Meter (Main) | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0759 | EE | Multifunction Power Meter (Main) | GEN-1 | Basement (Genset) | Generator Common Trip | DI | Auxiliary Contact | EE Contractor | DRC-004-2024 EE/Multifunction Power Meter (Main) | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0760 | EE | Multifunction Power Meter (Main) | GEN-1 | Basement (Genset) | Generator Common Alarm | DI | Auxiliary Contact | EE Contractor | DRC-004-2024 EE/Multifunction Power Meter (Main) | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0761 | EE | Multifunction Power Meter (Main) | ATS-1 | Basement (Genset) | ATS Position (Mains/Gen) | DI | Auxiliary Contact | EE Contractor | DRC-004-2024 EE/Multifunction Power Meter (Main) | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)
P0762 | EE | Multifunction Power Meter (Main) | ATS-1 | Basement (Genset) | ATS Trip | DI | Auxiliary Contact | EE Contractor | DRC-004-2024 EE/Multifunction Power Meter (Main) | FCP-BSMT | Synthesized from DRC-004-2024 (DRC standards) + TUEC BMS-01..03 (quantities)