## Summary
A2 — Equipment Takeoff Summary
Total instances | 125
By equipment class
Exhaust Fan (Toilet) | 32
Exhaust Fan (General) | 17
AHU (Chilled-Water-Served) | 10
Precooled Air Handling Unit | 8
Multifunction Power Meter (Feeder) | 7
Heat Pump | 6
Calorifier (Hot Water Storage Tank) | 6
Recirculating Pump | 6
Multifunction Power Meter (Main) | 4
Chiller (Package Water-Cooled) | 3
Cooling Tower | 3
DOAS Unit | 3
Primary CHW Pump | 3
Condenser Water Pump | 3
AHU (Modulating CHW-served) | 2
Steam Boiler | 2
Hot Water Header Set | 2
Ozone Generator (UV-light or Corona) | 2
CHW Bypass Header | 1
CHW Return Main Header | 1
CHW Supply Main Header | 1
Condenser Water Header | 1
Cooling Tower (Common) | 1
Primary CHW Pump (Standby) | 1
By location
2nd Floor | 25
2nd Floor (Plant Room) | 22
3rd Floor (Guestroom) | 20
Roofdeck | 19
Ground Floor | 12
Lower Ground | 12
3rd Floor (Amenity) | 7
2nd Floor (Casino) | 5
Basement (Genset) | 2
Basement | 1
By panel
FCP-2F | 30
FCP-3F | 27
MCP-PLANT | 22
FCP-RD | 19
FCP-BSMT | 15
FCP-GF | 12

## Equipment Takeoff
ID | Equipment Class | Quantity | Location | System | Panel | Primary C/O | Physical I/O | HLI Subpoints | Network Drops | Total I/O | Make/Model Assumed | Network Type | Typical Supplier | Notes
AHU-1.1 | AHU (Chilled-Water-Served) | 1 | Ground Floor | AC | FCP-GF | Equipment Supplier | 12 | 2 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-1.2 | AHU (Chilled-Water-Served) | 1 | Ground Floor | AC | FCP-GF | Equipment Supplier | 12 | 2 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-1.3 | AHU (Chilled-Water-Served) | 1 | Ground Floor | AC | FCP-GF | Equipment Supplier | 12 | 2 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-2M.1 | AHU (Modulating CHW-served) | 1 | 2nd Floor (Casino) | AC | FCP-2F | BMS Contractor | 15 | 2 | 0 | 17 | Modulating CHW-served AHU with VFD, modulating valve and dampers (position feedback) | Hardwired (VFD via BACnet HLI) | Mechanical contractor | Casino-spec AHU — modulating actuators with position feedback; CO/CO2 monitoring at return duct.
AHU-2M.2 | AHU (Modulating CHW-served) | 1 | 2nd Floor (Casino) | AC | FCP-2F | BMS Contractor | 15 | 2 | 0 | 17 | Modulating CHW-served AHU with VFD, modulating valve and dampers (position feedback) | Hardwired (VFD via BACnet HLI) | Mechanical contractor | Casino-spec AHU — modulating actuators with position feedback; CO/CO2 monitoring at return duct.
AHU-B.1 | AHU (Chilled-Water-Served) | 1 | 2nd Floor | AC | FCP-2F | Equipment Supplier | 12 | 2 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-B.2 | AHU (Chilled-Water-Served) | 1 | 2nd Floor | AC | FCP-2F | Equipment Supplier | 12 | 2 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-B.3 | AHU (Chilled-Water-Served) | 1 | 2nd Floor | AC | FCP-2F | Equipment Supplier | 12 | 2 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-EL | AHU (Chilled-Water-Served) | 1 | 2nd Floor | AC | FCP-2F | Equipment Supplier | 12 | 2 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-FR2 | AHU (Chilled-Water-Served) | 1 | 2nd Floor | AC | FCP-2F | Equipment Supplier | 12 | 2 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-FR3 | AHU (Chilled-Water-Served) | 1 | 2nd Floor | AC | FCP-2F | Equipment Supplier | 12 | 2 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-PF | AHU (Chilled-Water-Served) | 1 | 2nd Floor | AC | FCP-2F | Equipment Supplier | 12 | 2 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
ATS-1 | Multifunction Power Meter (Main) | 1 | Basement (Genset) | EE | FCP-BSMT | EE Contractor | 2 | 0 | 0 | 2 | Multifunction power meter with Modbus output (Schneider PM-series, ABB M2M, Siemens SENTRON), main switchgear class | Modbus RTU/TCP | BMS contractor | Mounted in main switchgear or on dedicated BMS-side panel.
BLR-1 | Steam Boiler | 1 | Lower Ground | VENT | FCP-BSMT | Equipment Supplier | 16 | 0 | 0 | 16 | Fire-tube steam boiler with multi-stage burner, fuel-oil fired (typical for hotel laundry) | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies steam pressure, feedwater T, fluegas T+O2 sensors. Boiler equipment provides aux contacts for status/HOA/trip points.
BLR-2 | Steam Boiler | 1 | Lower Ground | VENT | FCP-BSMT | Equipment Supplier | 16 | 0 | 0 | 16 | Fire-tube steam boiler with multi-stage burner, fuel-oil fired (typical for hotel laundry) | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies steam pressure, feedwater T, fluegas T+O2 sensors. Boiler equipment provides aux contacts for status/HOA/trip points.
CH-1 | Chiller (Package Water-Cooled) | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | Equipment Supplier | 11 | 18 | 1 | 30 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CH-2 | Chiller (Package Water-Cooled) | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | Equipment Supplier | 11 | 18 | 1 | 30 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CH-3 | Chiller (Package Water-Cooled) | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | Equipment Supplier | 11 | 18 | 1 | 30 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CHW-BYPASS | CHW Bypass Header | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | BMS Contractor | 4 | 0 | 0 | 4 | BMS dP/dT sensors + motorized bypass valve (BMS-supplied) | Hardwired | BMS contractor | BMS controls bypass valve to maintain CHW differential.
CHW-HDR-R | CHW Return Main Header | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | BMS Contractor | 2 | 0 | 0 | 2 | BMS T+P sensors on CHW return manifold | Hardwired | BMS contractor | Field instrumentation only.
CHW-HDR-S | CHW Supply Main Header | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | BMS Contractor | 2 | 0 | 0 | 2 | BMS T+P sensors on CHW supply manifold | Hardwired | BMS contractor | Field instrumentation only.
COW-HDR | Condenser Water Header | 1 | Roofdeck | AC | FCP-RD | BMS Contractor | 2 | 0 | 0 | 2 | BMS T sensors on condenser water headers at roofdeck | Hardwired | BMS contractor | Field instrumentation only.
CT-1 | Cooling Tower | 1 | Roofdeck | AC | FCP-RD | BMS Contractor | 7 | 0 | 0 | 7 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-2 | Cooling Tower | 1 | Roofdeck | AC | FCP-RD | BMS Contractor | 7 | 0 | 0 | 7 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-3 | Cooling Tower | 1 | Roofdeck | AC | FCP-RD | BMS Contractor | 7 | 0 | 0 | 7 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-COMMON | Cooling Tower (Common) | 1 | Roofdeck | AC | FCP-RD | BMS Contractor | 4 | 0 | 0 | 4 | Common BMS sensors at cooling tower area (OA T/RH, condenser headers) | Hardwired | BMS contractor | Field instrumentation only — no equipment per se.
DOAS-2M | DOAS Unit | 1 | 2nd Floor (Casino) | VENT | FCP-2F | Equipment Supplier | 20 | 4 | 1 | 25 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
DOAS-RD.1 | DOAS Unit | 1 | Roofdeck | VENT | FCP-RD | Equipment Supplier | 20 | 4 | 1 | 25 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
DOAS-RD.2 | DOAS Unit | 1 | Roofdeck | VENT | FCP-RD | Equipment Supplier | 20 | 4 | 1 | 25 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
EF-1.2A | Exhaust Fan (General) | 1 | Ground Floor | VENT | FCP-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-1MR.1 | Exhaust Fan (General) | 1 | Ground Floor | VENT | FCP-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-1ST0.1 | Exhaust Fan (General) | 1 | Ground Floor | VENT | FCP-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2.1 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2.2 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2.3 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2.4 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2B.1 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2B.2 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-3GE.1 | Exhaust Fan (General) | 1 | 3rd Floor (Amenity) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-3GE.2 | Exhaust Fan (General) | 1 | 3rd Floor (Amenity) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-CHR.1 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-CHR.2 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-GS.1 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-GS.2 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-LPG.1 | Exhaust Fan (General) | 1 | Ground Floor | VENT | FCP-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-MRF.1 | Exhaust Fan (General) | 1 | Ground Floor | VENT | FCP-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
GEN-1 | Multifunction Power Meter (Main) | 1 | Basement (Genset) | EE | FCP-BSMT | EE Contractor | 3 | 0 | 0 | 3 | Multifunction power meter with Modbus output (Schneider PM-series, ABB M2M, Siemens SENTRON), main switchgear class | Modbus RTU/TCP | BMS contractor | Mounted in main switchgear or on dedicated BMS-side panel.
HP-HZ.1 | Heat Pump | 1 | Roofdeck | HWL | FCP-RD | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-HZ.2 | Heat Pump | 1 | Roofdeck | HWL | FCP-RD | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-HZ.3 | Heat Pump | 1 | Roofdeck | HWL | FCP-RD | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-LZ.1 | Heat Pump | 1 | Lower Ground | HWL | FCP-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-LZ.2 | Heat Pump | 1 | Lower Ground | HWL | FCP-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-LZ.3 | Heat Pump | 1 | Lower Ground | HWL | FCP-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HW-HDR-HZ | Hot Water Header Set | 1 | Roofdeck | HWL | FCP-RD | BMS Contractor | 3 | 0 | 0 | 3 | Hot water supply/return manifolds with BMS T sensors and make-up cold water T sensor | Hardwired | BMS contractor | Field instrumentation on existing piping.
HW-HDR-LZ | Hot Water Header Set | 1 | Lower Ground | HWL | FCP-BSMT | BMS Contractor | 3 | 0 | 0 | 3 | Hot water supply/return manifolds with BMS T sensors and make-up cold water T sensor | Hardwired | BMS contractor | Field instrumentation on existing piping.
HWT-HZ.1 | Calorifier (Hot Water Storage Tank) | 1 | Roofdeck | HWL | FCP-RD | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-HZ.2 | Calorifier (Hot Water Storage Tank) | 1 | Roofdeck | HWL | FCP-RD | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-HZ.3 | Calorifier (Hot Water Storage Tank) | 1 | Roofdeck | HWL | FCP-RD | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-LZ.1 | Calorifier (Hot Water Storage Tank) | 1 | Lower Ground | HWL | FCP-BSMT | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-LZ.2 | Calorifier (Hot Water Storage Tank) | 1 | Lower Ground | HWL | FCP-BSMT | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-LZ.3 | Calorifier (Hot Water Storage Tank) | 1 | Lower Ground | HWL | FCP-BSMT | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
ION-2M.1 | Ozone Generator (UV-light or Corona) | 1 | 2nd Floor (Casino) | AC | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | UV-light or corona-discharge ozone generator (paired with Casino AHU) | Hardwired | Equipment supplier | Casino-specific air-treatment device. BMS monitors status/trip and reads VOC sensor (BMS-supplied).
ION-2M.2 | Ozone Generator (UV-light or Corona) | 1 | 2nd Floor (Casino) | AC | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | UV-light or corona-discharge ozone generator (paired with Casino AHU) | Hardwired | Equipment supplier | Casino-specific air-treatment device. BMS monitors status/trip and reads VOC sensor (BMS-supplied).
PAHU-0.1 | Precooled Air Handling Unit | 1 | Basement | VENT | FCP-BSMT | Equipment Supplier | 11 | 2 | 1 | 14 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-B1 | Precooled Air Handling Unit | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 11 | 2 | 1 | 14 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-B2 | Precooled Air Handling Unit | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 11 | 2 | 1 | 14 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-B3 | Precooled Air Handling Unit | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 11 | 2 | 1 | 14 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-FR | Precooled Air Handling Unit | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 11 | 2 | 1 | 14 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-PF | Precooled Air Handling Unit | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 11 | 2 | 1 | 14 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-RD.1 | Precooled Air Handling Unit | 1 | Roofdeck | VENT | FCP-RD | Equipment Supplier | 11 | 2 | 1 | 14 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-RD.2 | Precooled Air Handling Unit | 1 | Roofdeck | VENT | FCP-RD | Equipment Supplier | 11 | 2 | 1 | 14 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PCHW-1 | Primary CHW Pump | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | Equipment Supplier | 4 | 1 | 0 | 5 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
PCHW-2 | Primary CHW Pump | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | Equipment Supplier | 4 | 1 | 0 | 5 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
PCHW-3 | Primary CHW Pump | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | Equipment Supplier | 4 | 1 | 0 | 5 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
PCHW-S | Primary CHW Pump (Standby) | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | Equipment Supplier | 4 | 1 | 0 | 5 | Same as Primary CHW Pump (1 standby for N+1 redundancy) | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | Standby unit per A-CHW-001.
PCOW-1 | Condenser Water Pump | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | Equipment Supplier | 3 | 0 | 0 | 3 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
PCOW-2 | Condenser Water Pump | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | Equipment Supplier | 3 | 0 | 0 | 3 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
PCOW-3 | Condenser Water Pump | 1 | 2nd Floor (Plant Room) | AC | MCP-PLANT | Equipment Supplier | 3 | 0 | 0 | 3 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
PM-GEN | Multifunction Power Meter (Main) | 1 | 2nd Floor (Plant Room) | EE | MCP-PLANT | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output (Schneider PM-series, ABB M2M, Siemens SENTRON), main switchgear class | Modbus RTU/TCP | BMS contractor | Mounted in main switchgear or on dedicated BMS-side panel.
PM-MAIN | Multifunction Power Meter (Main) | 1 | 2nd Floor (Plant Room) | EE | MCP-PLANT | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output (Schneider PM-series, ABB M2M, Siemens SENTRON), main switchgear class | Modbus RTU/TCP | BMS contractor | Mounted in main switchgear or on dedicated BMS-side panel.
PM-MCC-BOILER | Multifunction Power Meter (Feeder) | 1 | 2nd Floor (Plant Room) | EE | MCP-PLANT | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-MCC-CHILLER | Multifunction Power Meter (Feeder) | 1 | 2nd Floor (Plant Room) | EE | MCP-PLANT | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-MCC-CT | Multifunction Power Meter (Feeder) | 1 | 2nd Floor (Plant Room) | EE | MCP-PLANT | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-MCC-FIRE-PUMP | Multifunction Power Meter (Feeder) | 1 | 2nd Floor (Plant Room) | EE | MCP-PLANT | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-MCC-MDP-1 | Multifunction Power Meter (Feeder) | 1 | 2nd Floor (Plant Room) | EE | MCP-PLANT | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-MCC-MDP-2 | Multifunction Power Meter (Feeder) | 1 | 2nd Floor (Plant Room) | EE | MCP-PLANT | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-MCC-MDP-3 | Multifunction Power Meter (Feeder) | 1 | 2nd Floor (Plant Room) | EE | MCP-PLANT | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
RP-HZ.1 | Recirculating Pump | 1 | Roofdeck | HWL | FCP-RD | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-HZ.2 | Recirculating Pump | 1 | Roofdeck | HWL | FCP-RD | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-HZ.3 | Recirculating Pump | 1 | Roofdeck | HWL | FCP-RD | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-LZ.1 | Recirculating Pump | 1 | Lower Ground | HWL | FCP-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-LZ.2 | Recirculating Pump | 1 | Lower Ground | HWL | FCP-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-LZ.3 | Recirculating Pump | 1 | Lower Ground | HWL | FCP-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
TEF-1.1 | Exhaust Fan (Toilet) | 1 | Ground Floor | VENT | FCP-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-1.2 | Exhaust Fan (Toilet) | 1 | Ground Floor | VENT | FCP-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-1.3 | Exhaust Fan (Toilet) | 1 | Ground Floor | VENT | FCP-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-1.4 | Exhaust Fan (Toilet) | 1 | Ground Floor | VENT | FCP-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2.1 | Exhaust Fan (Toilet) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2.3 | Exhaust Fan (Toilet) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2B.3 | Exhaust Fan (Toilet) | 1 | 2nd Floor | VENT | FCP-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3A.1 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Amenity) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3A.2 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Amenity) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3B.1 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Amenity) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3C.1 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Amenity) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3C.2 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Amenity) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.1 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.10 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.11 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.12 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.13 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.14 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.15 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.16 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.17 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.18 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.19 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.2 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.20 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.3 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.4 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.5 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.6 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.7 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.8 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.9 | Exhaust Fan (Toilet) | 1 | 3rd Floor (Guestroom) | VENT | FCP-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.