## Summary
A3 — Cable Schedule Summary
Total field cable runs | 198
Total field cable length (m) | 5940
Total trunk cable length (m) | 660
Total power feed length (m) | 180
GRAND TOTAL cable length (m) | 6780
By cable type (m)
4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2940
4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 1380
4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 870
Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 690
Modbus shielded twisted-pair, 1pr × 22 AWG (e.g., Belden 9841) | 60

## Field Cables
ID | From | To | Equipment Class | System | Location | Cable Type | Conductors Required | Conductors Specified | Length (m) | I/O Points Carried | Notes
C0001 | FCP-GF | AHU-1.1 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | Ground Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0002 | FCP-GF | AHU-1.1 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | Ground Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0003 | FCP-GF | AHU-1.1 (ME Contractor) | AHU (Chilled-Water-Served) | AC | Ground Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0004 | FCP-GF | AHU-1.2 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | Ground Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0005 | FCP-GF | AHU-1.2 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | Ground Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0006 | FCP-GF | AHU-1.2 (ME Contractor) | AHU (Chilled-Water-Served) | AC | Ground Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0007 | FCP-GF | AHU-1.3 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | Ground Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0008 | FCP-GF | AHU-1.3 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | Ground Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0009 | FCP-GF | AHU-1.3 (ME Contractor) | AHU (Chilled-Water-Served) | AC | Ground Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0010 | FCP-2F | AHU-2M.1 (BMS Contractor) | AHU (Modulating CHW-served) | AC | 2nd Floor (Casino) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 10 | 12 | 30 | 8 | 8 I/O points carried, 12C cable per A-001 (avg 30 m)
C0011 | FCP-2F | AHU-2M.1 (Equipment Supplier) | AHU (Modulating CHW-served) | AC | 2nd Floor (Casino) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0012 | FCP-2F | AHU-2M.1 (ME Contractor) | AHU (Modulating CHW-served) | AC | 2nd Floor (Casino) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0013 | FCP-2F | AHU-2M.2 (BMS Contractor) | AHU (Modulating CHW-served) | AC | 2nd Floor (Casino) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 10 | 12 | 30 | 8 | 8 I/O points carried, 12C cable per A-001 (avg 30 m)
C0014 | FCP-2F | AHU-2M.2 (Equipment Supplier) | AHU (Modulating CHW-served) | AC | 2nd Floor (Casino) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0015 | FCP-2F | AHU-2M.2 (ME Contractor) | AHU (Modulating CHW-served) | AC | 2nd Floor (Casino) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0016 | FCP-2F | AHU-B.1 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0017 | FCP-2F | AHU-B.1 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0018 | FCP-2F | AHU-B.1 (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0019 | FCP-2F | AHU-B.2 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0020 | FCP-2F | AHU-B.2 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0021 | FCP-2F | AHU-B.2 (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0022 | FCP-2F | AHU-B.3 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0023 | FCP-2F | AHU-B.3 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0024 | FCP-2F | AHU-B.3 (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0025 | FCP-2F | AHU-EL (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0026 | FCP-2F | AHU-EL (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0027 | FCP-2F | AHU-EL (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0028 | FCP-2F | AHU-FR2 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0029 | FCP-2F | AHU-FR2 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0030 | FCP-2F | AHU-FR2 (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0031 | FCP-2F | AHU-FR3 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0032 | FCP-2F | AHU-FR3 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0033 | FCP-2F | AHU-FR3 (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0034 | FCP-2F | AHU-PF (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0035 | FCP-2F | AHU-PF (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0036 | FCP-2F | AHU-PF (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0037 | FCP-BSMT | ATS-1 (EE Contractor) | Multifunction Power Meter (Main) | EE | Basement (Genset) | Modbus shielded twisted-pair, 1pr × 22 AWG (e.g., Belden 9841) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0038 | FCP-BSMT | BLR-1 (BMS Contractor) | Steam Boiler | VENT | Lower Ground | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable per A-001 (avg 30 m)
C0039 | FCP-BSMT | BLR-1 (Equipment Supplier) | Steam Boiler | VENT | Lower Ground | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | 12 | 30 | 10 | 10 I/O points carried, 12C cable per A-001 (avg 30 m)
C0040 | FCP-BSMT | BLR-2 (BMS Contractor) | Steam Boiler | VENT | Lower Ground | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable per A-001 (avg 30 m)
C0041 | FCP-BSMT | BLR-2 (Equipment Supplier) | Steam Boiler | VENT | Lower Ground | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | 12 | 30 | 10 | 10 I/O points carried, 12C cable per A-001 (avg 30 m)
C0042 | MCP-PLANT | CH-1 (BMS Contractor) | Chiller (Package Water-Cooled) | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 9 | 12 | 30 | 7 | 7 I/O points carried, 12C cable per A-001 (avg 30 m)
C0043 | MCP-PLANT | CH-1 (ME Contractor) | Chiller (Package Water-Cooled) | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0044 | MCP-PLANT | CH-2 (BMS Contractor) | Chiller (Package Water-Cooled) | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 9 | 12 | 30 | 7 | 7 I/O points carried, 12C cable per A-001 (avg 30 m)
C0045 | MCP-PLANT | CH-2 (ME Contractor) | Chiller (Package Water-Cooled) | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0046 | MCP-PLANT | CH-3 (BMS Contractor) | Chiller (Package Water-Cooled) | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 9 | 12 | 30 | 7 | 7 I/O points carried, 12C cable per A-001 (avg 30 m)
C0047 | MCP-PLANT | CH-3 (ME Contractor) | Chiller (Package Water-Cooled) | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0048 | MCP-PLANT | CHW-BYPASS (BMS Contractor) | CHW Bypass Header | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0049 | MCP-PLANT | CHW-HDR-R (BMS Contractor) | CHW Return Main Header | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0050 | MCP-PLANT | CHW-HDR-S (BMS Contractor) | CHW Supply Main Header | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0051 | FCP-RD | COW-HDR (BMS Contractor) | Condenser Water Header | AC | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0052 | FCP-RD | CT-1 (BMS Contractor) | Cooling Tower | AC | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0053 | FCP-RD | CT-1 (Equipment Supplier) | Cooling Tower | AC | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0054 | FCP-RD | CT-1 (ME Contractor) | Cooling Tower | AC | Roofdeck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0055 | FCP-RD | CT-2 (BMS Contractor) | Cooling Tower | AC | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0056 | FCP-RD | CT-2 (Equipment Supplier) | Cooling Tower | AC | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0057 | FCP-RD | CT-2 (ME Contractor) | Cooling Tower | AC | Roofdeck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0058 | FCP-RD | CT-3 (BMS Contractor) | Cooling Tower | AC | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0059 | FCP-RD | CT-3 (Equipment Supplier) | Cooling Tower | AC | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0060 | FCP-RD | CT-3 (ME Contractor) | Cooling Tower | AC | Roofdeck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0061 | FCP-RD | CT-COMMON (BMS Contractor) | Cooling Tower (Common) | AC | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0062 | FCP-2F | DOAS-2M (BMS Contractor) | DOAS Unit | VENT | 2nd Floor (Casino) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable per A-001 (avg 30 m)
C0063 | FCP-2F | DOAS-2M (Equipment Supplier) | DOAS Unit | VENT | 2nd Floor (Casino) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | 12 | 30 | 10 | 10 I/O points carried, 12C cable per A-001 (avg 30 m)
C0064 | FCP-2F | DOAS-2M (ME Contractor) | DOAS Unit | VENT | 2nd Floor (Casino) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0065 | FCP-RD | DOAS-RD.1 (BMS Contractor) | DOAS Unit | VENT | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable per A-001 (avg 30 m)
C0066 | FCP-RD | DOAS-RD.1 (Equipment Supplier) | DOAS Unit | VENT | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | 12 | 30 | 10 | 10 I/O points carried, 12C cable per A-001 (avg 30 m)
C0067 | FCP-RD | DOAS-RD.1 (ME Contractor) | DOAS Unit | VENT | Roofdeck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0068 | FCP-RD | DOAS-RD.2 (BMS Contractor) | DOAS Unit | VENT | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable per A-001 (avg 30 m)
C0069 | FCP-RD | DOAS-RD.2 (Equipment Supplier) | DOAS Unit | VENT | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | 12 | 30 | 10 | 10 I/O points carried, 12C cable per A-001 (avg 30 m)
C0070 | FCP-RD | DOAS-RD.2 (ME Contractor) | DOAS Unit | VENT | Roofdeck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0071 | FCP-GF | EF-1.2A (Equipment Supplier) | Exhaust Fan (General) | VENT | Ground Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0072 | FCP-GF | EF-1MR.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Ground Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0073 | FCP-GF | EF-1ST0.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Ground Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0074 | FCP-2F | EF-2.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0075 | FCP-2F | EF-2.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0076 | FCP-2F | EF-2.3 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0077 | FCP-2F | EF-2.4 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0078 | FCP-2F | EF-2B.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0079 | FCP-2F | EF-2B.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0080 | FCP-3F | EF-3GE.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | 3rd Floor (Amenity) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0081 | FCP-3F | EF-3GE.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | 3rd Floor (Amenity) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0082 | FCP-2F | EF-CHR.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0083 | FCP-2F | EF-CHR.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0084 | FCP-2F | EF-GS.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0085 | FCP-2F | EF-GS.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0086 | FCP-GF | EF-LPG.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Ground Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0087 | FCP-GF | EF-MRF.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Ground Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0088 | FCP-BSMT | GEN-1 (EE Contractor) | Multifunction Power Meter (Main) | EE | Basement (Genset) | Modbus shielded twisted-pair, 1pr × 22 AWG (e.g., Belden 9841) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0089 | FCP-RD | HP-HZ.1 (Equipment Supplier) | Heat Pump | HWL | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0090 | FCP-RD | HP-HZ.2 (Equipment Supplier) | Heat Pump | HWL | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0091 | FCP-RD | HP-HZ.3 (Equipment Supplier) | Heat Pump | HWL | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0092 | FCP-BSMT | HP-LZ.1 (Equipment Supplier) | Heat Pump | HWL | Lower Ground | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0093 | FCP-BSMT | HP-LZ.2 (Equipment Supplier) | Heat Pump | HWL | Lower Ground | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0094 | FCP-BSMT | HP-LZ.3 (Equipment Supplier) | Heat Pump | HWL | Lower Ground | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0095 | FCP-RD | HW-HDR-HZ (BMS Contractor) | Hot Water Header Set | HWL | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0096 | FCP-BSMT | HW-HDR-LZ (BMS Contractor) | Hot Water Header Set | HWL | Lower Ground | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0097 | FCP-RD | HWT-HZ.1 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | HWL | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable per A-001 (avg 30 m)
C0098 | FCP-RD | HWT-HZ.2 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | HWL | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable per A-001 (avg 30 m)
C0099 | FCP-RD | HWT-HZ.3 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | HWL | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable per A-001 (avg 30 m)
C0100 | FCP-BSMT | HWT-LZ.1 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | HWL | Lower Ground | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable per A-001 (avg 30 m)
C0101 | FCP-BSMT | HWT-LZ.2 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | HWL | Lower Ground | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable per A-001 (avg 30 m)
C0102 | FCP-BSMT | HWT-LZ.3 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | HWL | Lower Ground | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable per A-001 (avg 30 m)
C0103 | FCP-2F | ION-2M.1 (BMS Contractor) | Ozone Generator (UV-light or Corona) | AC | 2nd Floor (Casino) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable per A-001 (avg 30 m)
C0104 | FCP-2F | ION-2M.1 (Equipment Supplier) | Ozone Generator (UV-light or Corona) | AC | 2nd Floor (Casino) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0105 | FCP-2F | ION-2M.2 (BMS Contractor) | Ozone Generator (UV-light or Corona) | AC | 2nd Floor (Casino) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable per A-001 (avg 30 m)
C0106 | FCP-2F | ION-2M.2 (Equipment Supplier) | Ozone Generator (UV-light or Corona) | AC | 2nd Floor (Casino) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0107 | FCP-BSMT | PAHU-0.1 (BMS Contractor) | Precooled Air Handling Unit | VENT | Basement | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0108 | FCP-BSMT | PAHU-0.1 (Equipment Supplier) | Precooled Air Handling Unit | VENT | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0109 | FCP-BSMT | PAHU-0.1 (ME Contractor) | Precooled Air Handling Unit | VENT | Basement | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0110 | FCP-2F | PAHU-B1 (BMS Contractor) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0111 | FCP-2F | PAHU-B1 (Equipment Supplier) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0112 | FCP-2F | PAHU-B1 (ME Contractor) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0113 | FCP-2F | PAHU-B2 (BMS Contractor) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0114 | FCP-2F | PAHU-B2 (Equipment Supplier) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0115 | FCP-2F | PAHU-B2 (ME Contractor) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0116 | FCP-2F | PAHU-B3 (BMS Contractor) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0117 | FCP-2F | PAHU-B3 (Equipment Supplier) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0118 | FCP-2F | PAHU-B3 (ME Contractor) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0119 | FCP-2F | PAHU-FR (BMS Contractor) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0120 | FCP-2F | PAHU-FR (Equipment Supplier) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0121 | FCP-2F | PAHU-FR (ME Contractor) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0122 | FCP-2F | PAHU-PF (BMS Contractor) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0123 | FCP-2F | PAHU-PF (Equipment Supplier) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0124 | FCP-2F | PAHU-PF (ME Contractor) | Precooled Air Handling Unit | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0125 | FCP-RD | PAHU-RD.1 (BMS Contractor) | Precooled Air Handling Unit | VENT | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0126 | FCP-RD | PAHU-RD.1 (Equipment Supplier) | Precooled Air Handling Unit | VENT | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0127 | FCP-RD | PAHU-RD.1 (ME Contractor) | Precooled Air Handling Unit | VENT | Roofdeck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0128 | FCP-RD | PAHU-RD.2 (BMS Contractor) | Precooled Air Handling Unit | VENT | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0129 | FCP-RD | PAHU-RD.2 (Equipment Supplier) | Precooled Air Handling Unit | VENT | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable per A-001 (avg 30 m)
C0130 | FCP-RD | PAHU-RD.2 (ME Contractor) | Precooled Air Handling Unit | VENT | Roofdeck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable per A-001 (avg 30 m)
C0131 | MCP-PLANT | PCHW-1 (Equipment Supplier) | Primary CHW Pump | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0132 | MCP-PLANT | PCHW-2 (Equipment Supplier) | Primary CHW Pump | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0133 | MCP-PLANT | PCHW-3 (Equipment Supplier) | Primary CHW Pump | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0134 | MCP-PLANT | PCHW-S (Equipment Supplier) | Primary CHW Pump (Standby) | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable per A-001 (avg 30 m)
C0135 | MCP-PLANT | PCOW-1 (Equipment Supplier) | Condenser Water Pump | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0136 | MCP-PLANT | PCOW-2 (Equipment Supplier) | Condenser Water Pump | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0137 | MCP-PLANT | PCOW-3 (Equipment Supplier) | Condenser Water Pump | AC | 2nd Floor (Plant Room) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0138 | FCP-RD | RP-HZ.1 (Equipment Supplier) | Recirculating Pump | HWL | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0139 | FCP-RD | RP-HZ.2 (Equipment Supplier) | Recirculating Pump | HWL | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0140 | FCP-RD | RP-HZ.3 (Equipment Supplier) | Recirculating Pump | HWL | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0141 | FCP-BSMT | RP-LZ.1 (Equipment Supplier) | Recirculating Pump | HWL | Lower Ground | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0142 | FCP-BSMT | RP-LZ.2 (Equipment Supplier) | Recirculating Pump | HWL | Lower Ground | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0143 | FCP-BSMT | RP-LZ.3 (Equipment Supplier) | Recirculating Pump | HWL | Lower Ground | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0144 | FCP-GF | TEF-1.1 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | Ground Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0145 | FCP-GF | TEF-1.2 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | Ground Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0146 | FCP-GF | TEF-1.3 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | Ground Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0147 | FCP-GF | TEF-1.4 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | Ground Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0148 | FCP-2F | TEF-2.1 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0149 | FCP-2F | TEF-2.3 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0150 | FCP-2F | TEF-2B.3 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0151 | FCP-3F | TEF-3A.1 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Amenity) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0152 | FCP-3F | TEF-3A.2 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Amenity) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0153 | FCP-3F | TEF-3B.1 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Amenity) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0154 | FCP-3F | TEF-3C.1 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Amenity) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0155 | FCP-3F | TEF-3C.2 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Amenity) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0156 | FCP-3F | TEF-3D.1 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0157 | FCP-3F | TEF-3D.10 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0158 | FCP-3F | TEF-3D.11 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0159 | FCP-3F | TEF-3D.12 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0160 | FCP-3F | TEF-3D.13 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0161 | FCP-3F | TEF-3D.14 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0162 | FCP-3F | TEF-3D.15 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0163 | FCP-3F | TEF-3D.16 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0164 | FCP-3F | TEF-3D.17 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0165 | FCP-3F | TEF-3D.18 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0166 | FCP-3F | TEF-3D.19 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0167 | FCP-3F | TEF-3D.2 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0168 | FCP-3F | TEF-3D.20 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0169 | FCP-3F | TEF-3D.3 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0170 | FCP-3F | TEF-3D.4 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0171 | FCP-3F | TEF-3D.5 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0172 | FCP-3F | TEF-3D.6 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0173 | FCP-3F | TEF-3D.7 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0174 | FCP-3F | TEF-3D.8 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0175 | FCP-3F | TEF-3D.9 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor (Guestroom) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable per A-001 (avg 30 m)
C0176 | FCP-BSMT | PAHU-0.1 (Network) | Precooled Air Handling Unit | VENT | Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0177 | FCP-2F | PAHU-B1 (Network) | Precooled Air Handling Unit | VENT | 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0178 | FCP-2F | PAHU-B2 (Network) | Precooled Air Handling Unit | VENT | 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0179 | FCP-2F | PAHU-B3 (Network) | Precooled Air Handling Unit | VENT | 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0180 | FCP-2F | PAHU-PF (Network) | Precooled Air Handling Unit | VENT | 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0181 | FCP-2F | PAHU-FR (Network) | Precooled Air Handling Unit | VENT | 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0182 | FCP-2F | DOAS-2M (Network) | DOAS Unit | VENT | 2nd Floor (Casino) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0183 | FCP-RD | DOAS-RD.1 (Network) | DOAS Unit | VENT | Roofdeck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0184 | FCP-RD | DOAS-RD.2 (Network) | DOAS Unit | VENT | Roofdeck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0185 | FCP-RD | PAHU-RD.1 (Network) | Precooled Air Handling Unit | VENT | Roofdeck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0186 | FCP-RD | PAHU-RD.2 (Network) | Precooled Air Handling Unit | VENT | Roofdeck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0187 | MCP-PLANT | CH-1 (Network) | Chiller (Package Water-Cooled) | AC | 2nd Floor (Plant Room) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0188 | MCP-PLANT | CH-2 (Network) | Chiller (Package Water-Cooled) | AC | 2nd Floor (Plant Room) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0189 | MCP-PLANT | CH-3 (Network) | Chiller (Package Water-Cooled) | AC | 2nd Floor (Plant Room) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0190 | MCP-PLANT | PM-MAIN (Network) | Multifunction Power Meter (Main) | EE | 2nd Floor (Plant Room) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0191 | MCP-PLANT | PM-GEN (Network) | Multifunction Power Meter (Main) | EE | 2nd Floor (Plant Room) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0192 | MCP-PLANT | PM-MCC-CHILLER (Network) | Multifunction Power Meter (Feeder) | EE | 2nd Floor (Plant Room) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0193 | MCP-PLANT | PM-MCC-CT (Network) | Multifunction Power Meter (Feeder) | EE | 2nd Floor (Plant Room) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0194 | MCP-PLANT | PM-MCC-BOILER (Network) | Multifunction Power Meter (Feeder) | EE | 2nd Floor (Plant Room) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0195 | MCP-PLANT | PM-MCC-FIRE-PUMP (Network) | Multifunction Power Meter (Feeder) | EE | 2nd Floor (Plant Room) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0196 | MCP-PLANT | PM-MCC-MDP-1 (Network) | Multifunction Power Meter (Feeder) | EE | 2nd Floor (Plant Room) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0197 | MCP-PLANT | PM-MCC-MDP-2 (Network) | Multifunction Power Meter (Feeder) | EE | 2nd Floor (Plant Room) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller
C0198 | MCP-PLANT | PM-MCC-MDP-3 (Network) | Multifunction Power Meter (Feeder) | EE | 2nd Floor (Plant Room) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller

## Trunks
ID | From | To | Cable Type | Length (m) | Notes
T0199 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for 2nd Floor — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0200 | BMS Server Room (head-end) | All BMS panels at 3rd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for 3rd Floor — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0201 | BMS Server Room (head-end) | All BMS panels at Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Basement — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0202 | BMS Server Room (head-end) | All BMS panels at Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Ground — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0203 | BMS Server Room (head-end) | All BMS panels at Lower Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Lower Ground — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0204 | BMS Server Room (head-end) | All BMS panels at Roofdeck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Roofdeck — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0205 | BMS Server Room (head-end) | All BMS panel controllers (MS/TP daisy-chain or branched) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 180 | MS/TP backbone interconnecting 6 BMS panels — refine after Q-008 layout review

## Panel Power Feeds
ID | From | To | Cable Type | Length (m) | Notes
P0206 | Local panelboard / EE-supplied feeder | FCP-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7)
P0207 | Local panelboard / EE-supplied feeder | FCP-3F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7)
P0208 | Local panelboard / EE-supplied feeder | FCP-BSMT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7)
P0209 | Local panelboard / EE-supplied feeder | FCP-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7)
P0210 | Local panelboard / EE-supplied feeder | FCP-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7)
P0211 | Local panelboard / EE-supplied feeder | MCP-PLANT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7)