## Summary
A4 — Panel Schedule Summary
Total panels | 6
Total physical I/O | 629
Total HLI subpoints | 110
Total network drops | 23
Total I/O points | 762
Estimated total controllers | 18
Estimated total power (W) | 565

## Panel Schedule
Panel | Location | System Scope | Equipment Count | Physical I/O | HLI Subpoints | Network Drops | Total I/O | DDC Controllers | Network Gateway | Total Controllers | Power (W) | Enclosure
FCP-2F | 2nd Floor / 2nd Floor (Casino) | AC, VENT | 30 | 234 | 32 | 6 | 272 | 6 | 1 | 6 | 180 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
FCP-3F | 3rd Floor (Amenity) / 3rd Floor (Guestroom) | VENT | 27 | 81 | 0 | 0 | 81 | 3 | 0 | 3 | 75 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
FCP-BSMT | Basement / Basement (Genset) / Lower Ground | EE, HWL, VENT | 15 | 72 | 2 | 1 | 75 | 2 | 1 | 2 | 55 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
FCP-GF | Ground Floor | AC, VENT | 12 | 63 | 6 | 0 | 69 | 2 | 0 | 2 | 50 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
FCP-RD | Roofdeck | AC, HWL, VENT | 19 | 113 | 12 | 4 | 129 | 3 | 1 | 3 | 95 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
MCP-PLANT | 2nd Floor (Plant Room) | AC, EE | 22 | 66 | 58 | 12 | 136 | 2 | 1 | 2 | 110 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare

## Equipment per Panel
Panel | Equipment Instance
FCP-2F | AHU-2M.1
FCP-2F | AHU-2M.2
FCP-2F | AHU-B.1
FCP-2F | AHU-B.2
FCP-2F | AHU-B.3
FCP-2F | AHU-EL
FCP-2F | AHU-FR2
FCP-2F | AHU-FR3
FCP-2F | AHU-PF
FCP-2F | DOAS-2M
FCP-2F | EF-2.1
FCP-2F | EF-2.2
FCP-2F | EF-2.3
FCP-2F | EF-2.4
FCP-2F | EF-2B.1
FCP-2F | EF-2B.2
FCP-2F | EF-CHR.1
FCP-2F | EF-CHR.2
FCP-2F | EF-GS.1
FCP-2F | EF-GS.2
FCP-2F | ION-2M.1
FCP-2F | ION-2M.2
FCP-2F | PAHU-B1
FCP-2F | PAHU-B2
FCP-2F | PAHU-B3
FCP-2F | PAHU-FR
FCP-2F | PAHU-PF
FCP-2F | TEF-2.1
FCP-2F | TEF-2.3
FCP-2F | TEF-2B.3
FCP-3F | EF-3GE.1
FCP-3F | EF-3GE.2
FCP-3F | TEF-3A.1
FCP-3F | TEF-3A.2
FCP-3F | TEF-3B.1
FCP-3F | TEF-3C.1
FCP-3F | TEF-3C.2
FCP-3F | TEF-3D.1
FCP-3F | TEF-3D.10
FCP-3F | TEF-3D.11
FCP-3F | TEF-3D.12
FCP-3F | TEF-3D.13
FCP-3F | TEF-3D.14
FCP-3F | TEF-3D.15
FCP-3F | TEF-3D.16
FCP-3F | TEF-3D.17
FCP-3F | TEF-3D.18
FCP-3F | TEF-3D.19
FCP-3F | TEF-3D.2
FCP-3F | TEF-3D.20
FCP-3F | TEF-3D.3
FCP-3F | TEF-3D.4
FCP-3F | TEF-3D.5
FCP-3F | TEF-3D.6
FCP-3F | TEF-3D.7
FCP-3F | TEF-3D.8
FCP-3F | TEF-3D.9
FCP-BSMT | ATS-1
FCP-BSMT | BLR-1
FCP-BSMT | BLR-2
FCP-BSMT | GEN-1
FCP-BSMT | HP-LZ.1
FCP-BSMT | HP-LZ.2
FCP-BSMT | HP-LZ.3
FCP-BSMT | HW-HDR-LZ
FCP-BSMT | HWT-LZ.1
FCP-BSMT | HWT-LZ.2
FCP-BSMT | HWT-LZ.3
FCP-BSMT | PAHU-0.1
FCP-BSMT | RP-LZ.1
FCP-BSMT | RP-LZ.2
FCP-BSMT | RP-LZ.3
FCP-GF | AHU-1.1
FCP-GF | AHU-1.2
FCP-GF | AHU-1.3
FCP-GF | EF-1.2A
FCP-GF | EF-1MR.1
FCP-GF | EF-1ST0.1
FCP-GF | EF-LPG.1
FCP-GF | EF-MRF.1
FCP-GF | TEF-1.1
FCP-GF | TEF-1.2
FCP-GF | TEF-1.3
FCP-GF | TEF-1.4
FCP-RD | COW-HDR
FCP-RD | CT-1
FCP-RD | CT-2
FCP-RD | CT-3
FCP-RD | CT-COMMON
FCP-RD | DOAS-RD.1
FCP-RD | DOAS-RD.2
FCP-RD | HP-HZ.1
FCP-RD | HP-HZ.2
FCP-RD | HP-HZ.3
FCP-RD | HW-HDR-HZ
FCP-RD | HWT-HZ.1
FCP-RD | HWT-HZ.2
FCP-RD | HWT-HZ.3
FCP-RD | PAHU-RD.1
FCP-RD | PAHU-RD.2
FCP-RD | RP-HZ.1
FCP-RD | RP-HZ.2
FCP-RD | RP-HZ.3
MCP-PLANT | CH-1
MCP-PLANT | CH-2
MCP-PLANT | CH-3
MCP-PLANT | CHW-BYPASS
MCP-PLANT | CHW-HDR-R
MCP-PLANT | CHW-HDR-S
MCP-PLANT | PCHW-1
MCP-PLANT | PCHW-2
MCP-PLANT | PCHW-3
MCP-PLANT | PCHW-S
MCP-PLANT | PCOW-1
MCP-PLANT | PCOW-2
MCP-PLANT | PCOW-3
MCP-PLANT | PM-GEN
MCP-PLANT | PM-MAIN
MCP-PLANT | PM-MCC-BOILER
MCP-PLANT | PM-MCC-CHILLER
MCP-PLANT | PM-MCC-CT
MCP-PLANT | PM-MCC-FIRE-PUMP
MCP-PLANT | PM-MCC-MDP-1
MCP-PLANT | PM-MCC-MDP-2
MCP-PLANT | PM-MCC-MDP-3