## Summary
A3 — Cable Schedule, Audit View
Project | Kingsford Hotel Bacolod — BMS (AB-Run-2)
Canonical source | A3-cable-schedule.yaml
How to record corrections | Edit the canonical YAML directly — add a verification: block to the affected row(s)
Totals
Total cables | 113
Total length (m) | 2,832
Field cables | 96
Trunk cables | 6
Panel power feeds | 11
Verification status
Status | Count | % of total
verified | 0 | 0%
needs_correction | 0 | 0%
uncertain | 0 | 0%
unverified | 113 | 100%
⚠ Known weak points
Cable lengths are estimates based on assumption A-001 (30 m average panel-to-device run, 80 m trunk per floor). Field-verified lengths typically vary by ±20% per cable. THIS IS THE SYSTEM'S WEAKEST AUTO-GENERATED QUANTITY — please verify before issuing the BOQ to the customer.
How corrections flow
1. Open A3-cable-schedule.yaml in any text editor.
2. Find the affected row by ID (column A in the Detail sheet).
3. Add a verification: block — see the 'Verification schema' sheet for the template.
4. Re-run: python3 _playbook/tools/generate-deliverables.py <project>
5. Corrections flow through B4 manhours, BOQ material costs, and final deliverables automatically.

## By Panel
Panel | Cable count | Total length (m)
PNL-AIR-2F | 15 | 450
PNL-CASINO-GF | 11 | 330
PNL-AIR-GF | 9 | 270
PNL-CH-PLANT-2F | 17 | 204
PNL-AIR-ROOF | 13 | 156
PNL-AIR-3F | 5 | 150
PNL-CT-ROOF | 8 | 102
PNL-PL-LG | 7 | 78
PNL-AIR-BSMT | 5 | 60
PNL-BLR-LG | 5 | 58
PNL-PM-LG | 1 | 12
TOTAL (field cables) | 96 | 1870

## By Floor
Floor | Cable count | Total length (m)
2nd Floor | 32 | 654
Ground | 20 | 600
Roofdeck | 21 | 258
3F Amenity | 5 | 150
Lower Ground | 13 | 148
Basement | 5 | 60
TOTAL | 96 | 1870

## By Cable Type
Cable type | Count | Total length (m)
4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 39 | 781
4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 28 | 507
4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 17 | 384
Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | 198

## Detail (cables)
ID | From | To | Cable type | Length (m) | Status | Corrected (m) | Verified by | Date | Drawing ref | Notes
C0001 | PNL-AIR-2F | AHU-2F-A (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0002 | PNL-AIR-2F | AHU-2F-A (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0003 | PNL-AIR-2F | AHU-2F-A (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0004 | PNL-AIR-2F | AHU-2F-B (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0005 | PNL-AIR-2F | AHU-2F-B (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0006 | PNL-AIR-2F | AHU-2F-B (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0007 | PNL-AIR-3F | AHU-3F-AM (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0008 | PNL-AIR-3F | AHU-3F-AM (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0009 | PNL-AIR-3F | AHU-3F-AM (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0010 | PNL-CASINO-GF | AHU-CASINO-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0011 | PNL-CASINO-GF | AHU-CASINO-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0012 | PNL-CASINO-GF | AHU-CASINO-1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0013 | PNL-CASINO-GF | AHU-CASINO-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0014 | PNL-CASINO-GF | AHU-CASINO-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0015 | PNL-CASINO-GF | AHU-CASINO-2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0016 | PNL-CASINO-GF | AHU-GF-CASINO (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0017 | PNL-CASINO-GF | AHU-GF-CASINO (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0018 | PNL-CASINO-GF | AHU-GF-CASINO (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0019 | PNL-AIR-GF | AHU-GF-LOB (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0020 | PNL-AIR-GF | AHU-GF-LOB (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0021 | PNL-AIR-GF | AHU-GF-LOB (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0022 | PNL-AIR-GF | AHU-GF-REST (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0023 | PNL-AIR-GF | AHU-GF-REST (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0024 | PNL-AIR-GF | AHU-GF-REST (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0025 | PNL-BLR-LG | BLR-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 10 | unverified
C0026 | PNL-BLR-LG | BLR-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0027 | PNL-BLR-LG | BLR-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0028 | PNL-BLR-LG | BLR-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0029 | PNL-PL-LG | CALOR-LG (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | unverified
C0030 | PNL-AIR-ROOF | CALOR-ROOF (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0031 | PNL-CH-PLANT-2F | CH-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 15 | unverified
C0032 | PNL-CH-PLANT-2F | CH-1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 12 | unverified
C0033 | PNL-CH-PLANT-2F | CH-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 18 | unverified
C0034 | PNL-CH-PLANT-2F | CH-2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 12 | unverified
C0035 | PNL-CH-PLANT-2F | CHW-BYP (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 10 | unverified
C0036 | PNL-CH-PLANT-2F | CHW-RET-HDR (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | unverified
C0037 | PNL-CH-PLANT-2F | CHW-SUP-HDR (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | unverified
C0038 | PNL-CH-PLANT-2F | CHWP-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 10 | unverified
C0039 | PNL-CH-PLANT-2F | CHWP-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 11 | unverified
C0040 | PNL-CH-PLANT-2F | CHWP-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0041 | PNL-CT-ROOF | CT-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0042 | PNL-CT-ROOF | CT-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 14 | unverified
C0043 | PNL-CT-ROOF | CT-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0044 | PNL-CT-ROOF | CT-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 16 | unverified
C0045 | PNL-CT-ROOF | CT-COMMON (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0046 | PNL-CT-ROOF | CT-COMMON (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 12 | unverified
C0047 | PNL-CT-ROOF | CW-HDR (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0048 | PNL-CH-PLANT-2F | CWP-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 13 | unverified
C0049 | PNL-CH-PLANT-2F | CWP-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 13 | unverified
C0050 | PNL-CH-PLANT-2F | CWP-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 14 | unverified
C0051 | PNL-AIR-2F | DOAS-2F (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0052 | PNL-AIR-2F | DOAS-2F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0053 | PNL-AIR-2F | DOAS-2F (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0054 | PNL-AIR-ROOF | DOAS-RD1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0055 | PNL-AIR-ROOF | DOAS-RD1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0056 | PNL-AIR-ROOF | DOAS-RD1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 12 | unverified
C0057 | PNL-AIR-ROOF | DOAS-RD2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0058 | PNL-AIR-ROOF | DOAS-RD2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0059 | PNL-AIR-ROOF | DOAS-RD2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 12 | unverified
C0060 | PNL-AIR-2F | EAS-GEN-2F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0061 | PNL-AIR-3F | EAS-GEN-3F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0062 | PNL-AIR-BSMT | EAS-GEN-BSMT (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0063 | PNL-AIR-GF | EAS-GEN-GF (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0064 | PNL-AIR-ROOF | EAS-GEN-ROOF (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0065 | PNL-AIR-2F | EAS-TOILET-2F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0066 | PNL-AIR-3F | EAS-TOILET-3F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0067 | PNL-AIR-BSMT | EAS-TOILET-BSMT (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0068 | PNL-AIR-GF | EAS-TOILET-GF (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0069 | PNL-PL-LG | HP-LG-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0070 | PNL-AIR-ROOF | HP-ROOF-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0071 | PNL-PL-LG | HW-HEADERS-LG (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 10 | unverified
C0072 | PNL-PL-LG | HW-PUMP-LG-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0073 | PNL-PL-LG | HW-PUMP-LG-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0074 | PNL-AIR-ROOF | HW-PUMP-ROOF-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0075 | PNL-CASINO-GF | OZ-CASINO-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0076 | PNL-AIR-2F | PAHU-2F (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0077 | PNL-AIR-2F | PAHU-2F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0078 | PNL-AIR-2F | PAHU-2F (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0079 | PNL-AIR-BSMT | PAHU-BSMT (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0080 | PNL-AIR-BSMT | PAHU-BSMT (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0081 | PNL-AIR-BSMT | PAHU-BSMT (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 12 | unverified
C0082 | PNL-AIR-ROOF | PAHU-ROOF (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0083 | PNL-AIR-ROOF | PAHU-ROOF (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0084 | PNL-AIR-ROOF | PAHU-ROOF (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 12 | unverified
C0085 | PNL-CH-PLANT-2F | CH-1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0086 | PNL-CH-PLANT-2F | CH-2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0087 | PNL-CH-PLANT-2F | BTU-CHW-MAIN (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0088 | PNL-PM-LG | PM-MAIN-LG (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0089 | PNL-CH-PLANT-2F | PM-CHILLER (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0090 | PNL-CT-ROOF | PM-COOLING (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0091 | PNL-AIR-2F | PM-AIR-2F (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0092 | PNL-AIR-GF | PM-AIR-GF (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0093 | PNL-CASINO-GF | PM-CASINO (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0094 | PNL-BLR-LG | PM-BOILER (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0095 | PNL-PL-LG | PM-PLUMB (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0096 | PNL-PL-LG | PM-FIREPMP (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
T0097 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0098 | BMS Server Room (head-end) | All BMS panels at Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0099 | BMS Server Room (head-end) | All BMS panels at Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0100 | BMS Server Room (head-end) | All BMS panels at Lower Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0101 | BMS Server Room (head-end) | All BMS panels at Roofdeck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0102 | BMS Server Room (head-end) | All BMS panel controllers (MS/TP daisy-chain or branched) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 330 | unverified
P0103 | Local panelboard / EE-supplied feeder | PNL-AIR-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0104 | Local panelboard / EE-supplied feeder | PNL-AIR-3F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0105 | Local panelboard / EE-supplied feeder | PNL-AIR-BSMT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0106 | Local panelboard / EE-supplied feeder | PNL-AIR-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0107 | Local panelboard / EE-supplied feeder | PNL-AIR-ROOF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 35 | unverified
P0108 | Local panelboard / EE-supplied feeder | PNL-BLR-LG — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0109 | Local panelboard / EE-supplied feeder | PNL-CASINO-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0110 | Local panelboard / EE-supplied feeder | PNL-CH-PLANT-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0111 | Local panelboard / EE-supplied feeder | PNL-CT-ROOF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 35 | unverified
P0112 | Local panelboard / EE-supplied feeder | PNL-PL-LG — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0113 | Local panelboard / EE-supplied feeder | PNL-PM-LG — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified

## Verification schema
How to record verification / corrections in A3-cable-schedule.yaml
Find the affected row in the YAML by ID (Detail sheet column A) and add a verification: block:
- id: C0001
from: PNL-CH-PLANT-GND
to: CH-1 (BMS Contractor)
cable_type: 4C × 1.5 mm² shielded FRLS
length_m: 30
verification: # ADDED by team
status: needs_correction # unverified ¦ verified ¦ needs_correction ¦ uncertain
corrected_length_m: 42 # team's measured / confirmed value
verified_by: J. Cruz
verified_date: 2026-05-10
drawing_ref: "EE-09 grid B-2"
notes: ""
After saving, re-run: python3 _playbook/tools/generate-deliverables.py <project>
Corrections propagate to B4 manhours, BOQ, and final deliverables automatically.
Recommended verification methods (priority order):
1. Site walkthrough with measurement (most accurate; for cable lengths, after structural completion).
2. Properly-scaled architectural drawings.
3. Mechanical contractor's tray layout combined with BMS panel locations.
4. A-001 default with ±20% contingency in BOQ — last resort.