## Summary
A1 — Consolidated I/O List Summary
Project | Kingsford Hotel Bacolod — BMS (AB-Run-2)
Total I/O rows | 474
By type
DI | 176
AI | 137
HLI | 79
AO | 56
DO | 14
Network | 12
By C/O
Equipment Supplier | 253
BMS Contractor | 165
ME Contractor | 56
By system
Ventilation | 108
Chilled Water Plant | 90
Air Conditioning | 84
Power Monitoring | 48
Condenser Water Loop | 34
Boiler | 32
Casino Air Conditioning | 31
Exhaust | 27
Hot Water | 20
By panel
PNL-CH-PLANT-2F | 107
PNL-AIR-2F | 75
PNL-AIR-ROOF | 70
PNL-CASINO-GF | 50
PNL-AIR-GF | 39
PNL-BLR-LG | 37
PNL-CT-ROOF | 27
PNL-PL-LG | 23
PNL-AIR-3F | 20
PNL-AIR-BSMT | 18
PNL-PM-LG | 8

## All IO Points
ID | System | Equipment Class | Equipment Instance | Location | Point Description | Type | Field Device | C/O | DoO Ref | Panel | Source | Notes
P0001 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Entering Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0002 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Leaving Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0003 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Entering Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0004 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Leaving Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0005 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Chilled Water Return Flow | AI | Flow Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0006 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Chilled Water Supply Flow | AI | Flow Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0007 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Condenser Water Supply Flow | AI | Flow Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0008 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | CHW Isolation Motorized Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0009 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | COW Isolation Motorized Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0010 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Chiller Native — comprehensive package data (HLI) | Network | Chiller Native BACnet IP | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0011 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Chiller Compressor Pump On/Off Status | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0012 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Chiller Compressor HOA Status | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0013 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Chiller Compressor Trip Alarm | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0014 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Motor Load Current | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0015 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Motor Consumption (kW/BTU) | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0016 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Winding Temperature | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0017 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Oil Pump Status | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0018 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Oil Pump Trip | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0019 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Oil Sump Pressure | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0020 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Oil Sump Temperature | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0021 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Evaporator Refrigerant Pressure | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0022 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Evaporator Refrigerant Temperature | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0023 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Evaporator Approach Δ Temperature | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0024 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Evaporator Approach Δ Pressure | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0025 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Condenser Refrigerant Pressure | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0026 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Condenser Refrigerant Temperature | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0027 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Condenser Approach Δ Temperature | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0028 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-1 | 2F Chiller Plant Room | Condenser Approach Δ Pressure | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 (Chillers @ 2nd Level) + MC-ME
P0029 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Entering Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0030 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Leaving Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0031 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Entering Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0032 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Leaving Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0033 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Chilled Water Return Flow | AI | Flow Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0034 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Chilled Water Supply Flow | AI | Flow Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0035 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Condenser Water Supply Flow | AI | Flow Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0036 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | CHW Isolation Motorized Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0037 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | COW Isolation Motorized Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0038 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Chiller Native — comprehensive package data (HLI) | Network | Chiller Native BACnet IP | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0039 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Chiller Compressor Pump On/Off Status | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0040 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Chiller Compressor HOA Status | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0041 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Chiller Compressor Trip Alarm | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0042 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Motor Load Current | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0043 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Motor Consumption (kW/BTU) | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0044 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Winding Temperature | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0045 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Oil Pump Status | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0046 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Oil Pump Trip | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0047 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Oil Sump Pressure | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0048 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Oil Sump Temperature | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0049 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Evaporator Refrigerant Pressure | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0050 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Evaporator Refrigerant Temperature | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0051 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Evaporator Approach Δ Temperature | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0052 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Evaporator Approach Δ Pressure | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0053 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Condenser Refrigerant Pressure | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0054 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Condenser Refrigerant Temperature | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0055 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Condenser Approach Δ Temperature | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0056 | Chilled Water Plant | Chiller (Package Water-Cooled) | CH-2 | 2F Chiller Plant Room | Condenser Approach Δ Pressure | HLI | Chiller Native | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0057 | Chilled Water Plant | Primary CHW Pump | CHWP-1 | 2F Chiller Plant Room | CHW Supply Pressure | AI | Pressure Sensor | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME (Primary CHW Circulating Pumps @ 2nd Level)
P0058 | Chilled Water Plant | Primary CHW Pump | CHWP-1 | 2F Chiller Plant Room | On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME (Primary CHW Circulating Pumps @ 2nd Level)
P0059 | Chilled Water Plant | Primary CHW Pump | CHWP-1 | 2F Chiller Plant Room | HOA Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME (Primary CHW Circulating Pumps @ 2nd Level)
P0060 | Chilled Water Plant | Primary CHW Pump | CHWP-1 | 2F Chiller Plant Room | VFD Speed Feedback | AI | VFD | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME (Primary CHW Circulating Pumps @ 2nd Level)
P0061 | Chilled Water Plant | Primary CHW Pump | CHWP-1 | 2F Chiller Plant Room | VFD Speed Command | AO | VFD | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME (Primary CHW Circulating Pumps @ 2nd Level)
P0062 | Chilled Water Plant | Primary CHW Pump | CHWP-1 | 2F Chiller Plant Room | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME (Primary CHW Circulating Pumps @ 2nd Level)
P0063 | Chilled Water Plant | Primary CHW Pump | CHWP-1 | 2F Chiller Plant Room | Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME (Primary CHW Circulating Pumps @ 2nd Level)
P0064 | Chilled Water Plant | Primary CHW Pump | CHWP-2 | 2F Chiller Plant Room | CHW Supply Pressure | AI | Pressure Sensor | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0065 | Chilled Water Plant | Primary CHW Pump | CHWP-2 | 2F Chiller Plant Room | On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0066 | Chilled Water Plant | Primary CHW Pump | CHWP-2 | 2F Chiller Plant Room | HOA Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0067 | Chilled Water Plant | Primary CHW Pump | CHWP-2 | 2F Chiller Plant Room | VFD Speed Feedback | AI | VFD | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0068 | Chilled Water Plant | Primary CHW Pump | CHWP-2 | 2F Chiller Plant Room | VFD Speed Command | AO | VFD | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0069 | Chilled Water Plant | Primary CHW Pump | CHWP-2 | 2F Chiller Plant Room | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0070 | Chilled Water Plant | Primary CHW Pump | CHWP-2 | 2F Chiller Plant Room | Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0071 | Chilled Water Plant | Primary CHW Pump (Standby) | CHWP-3 | 2F Chiller Plant Room | CHW Supply Pressure | AI | Pressure Sensor | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0072 | Chilled Water Plant | Primary CHW Pump (Standby) | CHWP-3 | 2F Chiller Plant Room | On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0073 | Chilled Water Plant | Primary CHW Pump (Standby) | CHWP-3 | 2F Chiller Plant Room | HOA Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0074 | Chilled Water Plant | Primary CHW Pump (Standby) | CHWP-3 | 2F Chiller Plant Room | VFD Speed Feedback | AI | VFD | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0075 | Chilled Water Plant | Primary CHW Pump (Standby) | CHWP-3 | 2F Chiller Plant Room | VFD Speed Command | AO | VFD | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0076 | Chilled Water Plant | Primary CHW Pump (Standby) | CHWP-3 | 2F Chiller Plant Room | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0077 | Chilled Water Plant | Primary CHW Pump (Standby) | CHWP-3 | 2F Chiller Plant Room | Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0078 | Condenser Water Loop | Condenser Water Pump | CWP-1 | 2F Chiller Plant Room | On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0079 | Condenser Water Loop | Condenser Water Pump | CWP-1 | 2F Chiller Plant Room | HOA Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0080 | Condenser Water Loop | Condenser Water Pump | CWP-1 | 2F Chiller Plant Room | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0081 | Condenser Water Loop | Condenser Water Pump | CWP-1 | 2F Chiller Plant Room | Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0082 | Condenser Water Loop | Condenser Water Pump | CWP-2 | 2F Chiller Plant Room | On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0083 | Condenser Water Loop | Condenser Water Pump | CWP-2 | 2F Chiller Plant Room | HOA Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0084 | Condenser Water Loop | Condenser Water Pump | CWP-2 | 2F Chiller Plant Room | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0085 | Condenser Water Loop | Condenser Water Pump | CWP-2 | 2F Chiller Plant Room | Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0086 | Condenser Water Loop | Condenser Water Pump | CWP-3 | 2F Chiller Plant Room | On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0087 | Condenser Water Loop | Condenser Water Pump | CWP-3 | 2F Chiller Plant Room | HOA Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0088 | Condenser Water Loop | Condenser Water Pump | CWP-3 | 2F Chiller Plant Room | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0089 | Condenser Water Loop | Condenser Water Pump | CWP-3 | 2F Chiller Plant Room | Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0090 | Chilled Water Plant | CHW Supply Main Header | CHW-SUP-HDR | 2F Chiller Plant Room | Header Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0091 | Chilled Water Plant | CHW Supply Main Header | CHW-SUP-HDR | 2F Chiller Plant Room | Header Pressure | AI | Pressure Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0092 | Chilled Water Plant | CHW Return Main Header | CHW-RET-HDR | 2F Chiller Plant Room | Header Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0093 | Chilled Water Plant | CHW Return Main Header | CHW-RET-HDR | 2F Chiller Plant Room | Header Pressure | AI | Pressure Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME
P0094 | Chilled Water Plant | CHW Bypass Header | CHW-BYP | 2F Chiller Plant Room | Differential Pressure | AI | Diff. Pressure Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME (CHW Main Header Supply & Return)
P0095 | Chilled Water Plant | CHW Bypass Header | CHW-BYP | 2F Chiller Plant Room | Differential Temperature | AI | Diff. Temp Sensor | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME (CHW Main Header Supply & Return)
P0096 | Chilled Water Plant | CHW Bypass Header | CHW-BYP | 2F Chiller Plant Room | CHW Bypass Isolation Valve Status | DI | Electric Valve Actuator | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME (CHW Main Header Supply & Return)
P0097 | Chilled Water Plant | CHW Bypass Header | CHW-BYP | 2F Chiller Plant Room | CHW Bypass Isolation Valve Command | DO | Electric Valve Actuator | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01 + MC-ME (CHW Main Header Supply & Return)
P0098 | Condenser Water Loop | Condenser Water Header | CW-HDR | Roofdeck Cooling Tower | Condenser Water Supply Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME
P0099 | Condenser Water Loop | Condenser Water Header | CW-HDR | Roofdeck Cooling Tower | Condenser Water Return Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME
P0100 | Chilled Water Plant | BTU Meter | BTU-CHW-MAIN | 2F Chiller Plant Room | BTU Meter HLI | Network | Modbus BTU Meter | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01
P0101 | Chilled Water Plant | BTU Meter | BTU-CHW-MAIN | 2F Chiller Plant Room | Energy (kWh/BTU) | HLI | Modbus BTU Meter | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01
P0102 | Chilled Water Plant | BTU Meter | BTU-CHW-MAIN | 2F Chiller Plant Room | Flow | HLI | Modbus BTU Meter | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01
P0103 | Chilled Water Plant | BTU Meter | BTU-CHW-MAIN | 2F Chiller Plant Room | Supply T | HLI | Modbus BTU Meter | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01
P0104 | Chilled Water Plant | BTU Meter | BTU-CHW-MAIN | 2F Chiller Plant Room | Return T | HLI | Modbus BTU Meter | BMS Contractor |  | PNL-CH-PLANT-2F | BMS-01
P0105 | Condenser Water Loop | Cooling Tower | CT-1 | Roofdeck Cooling Tower | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CT-ROOF | BMS-01 + MC-ME (Cooling Towers @ Roofdeck)
P0106 | Condenser Water Loop | Cooling Tower | CT-1 | Roofdeck Cooling Tower | Fan Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CT-ROOF | BMS-01 + MC-ME (Cooling Towers @ Roofdeck)
P0107 | Condenser Water Loop | Cooling Tower | CT-1 | Roofdeck Cooling Tower | Fan Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | PNL-CT-ROOF | BMS-01 + MC-ME (Cooling Towers @ Roofdeck)
P0108 | Condenser Water Loop | Cooling Tower | CT-1 | Roofdeck Cooling Tower | Basin Level Low Alarm | DI | Level Sensor / Electrode | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME (Cooling Towers @ Roofdeck)
P0109 | Condenser Water Loop | Cooling Tower | CT-1 | Roofdeck Cooling Tower | Basin Level High Alarm | DI | Level Sensor / Electrode | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME (Cooling Towers @ Roofdeck)
P0110 | Condenser Water Loop | Cooling Tower | CT-1 | Roofdeck Cooling Tower | Motorized Blowdown Valve Status | DI | Electric Valve Actuator | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME (Cooling Towers @ Roofdeck)
P0111 | Condenser Water Loop | Cooling Tower | CT-1 | Roofdeck Cooling Tower | Motorized Blowdown Valve Command | DO | Electric Valve Actuator | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME (Cooling Towers @ Roofdeck)
P0112 | Condenser Water Loop | Cooling Tower | CT-2 | Roofdeck Cooling Tower | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CT-ROOF | BMS-01 + MC-ME
P0113 | Condenser Water Loop | Cooling Tower | CT-2 | Roofdeck Cooling Tower | Fan Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CT-ROOF | BMS-01 + MC-ME
P0114 | Condenser Water Loop | Cooling Tower | CT-2 | Roofdeck Cooling Tower | Fan Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | PNL-CT-ROOF | BMS-01 + MC-ME
P0115 | Condenser Water Loop | Cooling Tower | CT-2 | Roofdeck Cooling Tower | Basin Level Low Alarm | DI | Level Sensor / Electrode | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME
P0116 | Condenser Water Loop | Cooling Tower | CT-2 | Roofdeck Cooling Tower | Basin Level High Alarm | DI | Level Sensor / Electrode | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME
P0117 | Condenser Water Loop | Cooling Tower | CT-2 | Roofdeck Cooling Tower | Motorized Blowdown Valve Status | DI | Electric Valve Actuator | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME
P0118 | Condenser Water Loop | Cooling Tower | CT-2 | Roofdeck Cooling Tower | Motorized Blowdown Valve Command | DO | Electric Valve Actuator | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME
P0119 | Condenser Water Loop | Cooling Tower (Common) | CT-COMMON | Roofdeck Cooling Tower | Outside Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME (basin level + OA T/RH + COW headers)
P0120 | Condenser Water Loop | Cooling Tower (Common) | CT-COMMON | Roofdeck Cooling Tower | Outside Air Humidity | AI | Humidity Sensor | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME (basin level + OA T/RH + COW headers)
P0121 | Condenser Water Loop | Cooling Tower (Common) | CT-COMMON | Roofdeck Cooling Tower | CW Return Header Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME (basin level + OA T/RH + COW headers)
P0122 | Condenser Water Loop | Cooling Tower (Common) | CT-COMMON | Roofdeck Cooling Tower | CW Supply Header Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME (basin level + OA T/RH + COW headers)
P0123 | Condenser Water Loop | Cooling Tower (Common) | CT-COMMON | Roofdeck Cooling Tower | Blowdown pH/Conductivity | AI | pH Sensor / Conductivity Sensor | ME Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME (basin level + OA T/RH + COW headers)
P0124 | Condenser Water Loop | Cooling Tower (Common) | CT-COMMON | Roofdeck Cooling Tower | COW Isolation Motorized Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-CT-ROOF | BMS-01 + MC-ME (basin level + OA T/RH + COW headers)
P0125 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Outdoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0126 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Outdoor Supply Air Flow | AI | Flow Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0127 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0128 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Indoor Mixed Air Temperature | AI | Temperature Sensor | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0129 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Indoor Mixed Air Humidity | AI | Humidity Sensor | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0130 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0131 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Indoor Exhaust Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0132 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Indoor Exhaust Air Humidity | AI | Humidity Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0133 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | OA Damper Status | DI | Damper Controller | ME Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0134 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | OA Damper Command | AO | Damper Controller | ME Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0135 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Recovery Wheel Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0136 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Recovery Wheel Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0137 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Supply Fan Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0138 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Supply Fan HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0139 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Supply Fan Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0140 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Supply Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0141 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Supply Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0142 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Exhaust Fan Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0143 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Exhaust Fan HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0144 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Exhaust Fan Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0145 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Exhaust Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0146 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | Exhaust Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0147 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | CHWS Coil Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0148 | Ventilation | DOAS Unit | DOAS-RD1 | Roofdeck DOAS | CHWS Coil Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck Serving Guestrooms RD1)
P0149 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Outdoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0150 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Outdoor Supply Air Flow | AI | Flow Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0151 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0152 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Indoor Mixed Air Temperature | AI | Temperature Sensor | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0153 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Indoor Mixed Air Humidity | AI | Humidity Sensor | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0154 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0155 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Indoor Exhaust Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0156 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Indoor Exhaust Air Humidity | AI | Humidity Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0157 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | OA Damper Status | DI | Damper Controller | ME Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0158 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | OA Damper Command | AO | Damper Controller | ME Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0159 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Recovery Wheel Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0160 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Recovery Wheel Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0161 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Supply Fan Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0162 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Supply Fan HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0163 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Supply Fan Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0164 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Supply Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0165 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Supply Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0166 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Exhaust Fan Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0167 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Exhaust Fan HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0168 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Exhaust Fan Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0169 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Exhaust Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0170 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | Exhaust Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0171 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | CHWS Coil Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0172 | Ventilation | DOAS Unit | DOAS-RD2 | Roofdeck DOAS | CHWS Coil Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-AIR-ROOF | MC-ME (DOAS @ Roofdeck RD2)
P0173 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Outdoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0174 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Outdoor Supply Air Flow | AI | Flow Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0175 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Outdoor Supply Air Humidity | AI | Humidity Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0176 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Indoor Mixed Air Temperature | AI | Temperature Sensor | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0177 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Indoor Mixed Air Humidity | AI | Humidity Sensor | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0178 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0179 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Indoor Exhaust Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0180 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Indoor Exhaust Air Humidity | AI | Humidity Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0181 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | OA Damper Status | DI | Damper Controller | ME Contractor |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0182 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | OA Damper Command | AO | Damper Controller | ME Contractor |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0183 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Recovery Wheel Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0184 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Recovery Wheel Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0185 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Supply Fan Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0186 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Supply Fan HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0187 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Supply Fan Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0188 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Supply Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0189 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Supply Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0190 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Exhaust Fan Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0191 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Exhaust Fan HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0192 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Exhaust Fan Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0193 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Exhaust Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0194 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | Exhaust Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0195 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | CHWS Coil Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0196 | Ventilation | DOAS Unit | DOAS-2F | 2F Common Public | CHWS Coil Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-AIR-2F | MC-ME (DOAS @ 2nd Level common/public)
P0197 | Ventilation | Precooled Air Handling Unit | PAHU-ROOF | Roofdeck DOAS | Outdoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (PAHU @ Roofdeck)
P0198 | Ventilation | Precooled Air Handling Unit | PAHU-ROOF | Roofdeck DOAS | Outdoor Supply Air Flow | AI | Flow Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (PAHU @ Roofdeck)
P0199 | Ventilation | Precooled Air Handling Unit | PAHU-ROOF | Roofdeck DOAS | OA Damper Status | DI | Damper Controller | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (PAHU @ Roofdeck)
P0200 | Ventilation | Precooled Air Handling Unit | PAHU-ROOF | Roofdeck DOAS | OA Damper Command | AO | Damper Controller | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (PAHU @ Roofdeck)
P0201 | Ventilation | Precooled Air Handling Unit | PAHU-ROOF | Roofdeck DOAS | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-ME (PAHU @ Roofdeck)
P0202 | Ventilation | Precooled Air Handling Unit | PAHU-ROOF | Roofdeck DOAS | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (PAHU @ Roofdeck)
P0203 | Ventilation | Precooled Air Handling Unit | PAHU-ROOF | Roofdeck DOAS | Fan Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (PAHU @ Roofdeck)
P0204 | Ventilation | Precooled Air Handling Unit | PAHU-ROOF | Roofdeck DOAS | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (PAHU @ Roofdeck)
P0205 | Ventilation | Precooled Air Handling Unit | PAHU-ROOF | Roofdeck DOAS | Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (PAHU @ Roofdeck)
P0206 | Ventilation | Precooled Air Handling Unit | PAHU-ROOF | Roofdeck DOAS | Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (PAHU @ Roofdeck)
P0207 | Ventilation | Precooled Air Handling Unit | PAHU-ROOF | Roofdeck DOAS | CHWS Coil Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-AIR-ROOF | MC-ME (PAHU @ Roofdeck)
P0208 | Ventilation | Precooled Air Handling Unit | PAHU-ROOF | Roofdeck DOAS | CHWS Coil Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-AIR-ROOF | MC-ME (PAHU @ Roofdeck)
P0209 | Ventilation | Precooled Air Handling Unit | PAHU-2F | 2F Common Public | Outdoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (PAHU @ 2nd Level)
P0210 | Ventilation | Precooled Air Handling Unit | PAHU-2F | 2F Common Public | Outdoor Supply Air Flow | AI | Flow Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (PAHU @ 2nd Level)
P0211 | Ventilation | Precooled Air Handling Unit | PAHU-2F | 2F Common Public | OA Damper Status | DI | Damper Controller | Equipment Supplier |  | PNL-AIR-2F | MC-ME (PAHU @ 2nd Level)
P0212 | Ventilation | Precooled Air Handling Unit | PAHU-2F | 2F Common Public | OA Damper Command | AO | Damper Controller | Equipment Supplier |  | PNL-AIR-2F | MC-ME (PAHU @ 2nd Level)
P0213 | Ventilation | Precooled Air Handling Unit | PAHU-2F | 2F Common Public | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (PAHU @ 2nd Level)
P0214 | Ventilation | Precooled Air Handling Unit | PAHU-2F | 2F Common Public | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (PAHU @ 2nd Level)
P0215 | Ventilation | Precooled Air Handling Unit | PAHU-2F | 2F Common Public | Fan Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (PAHU @ 2nd Level)
P0216 | Ventilation | Precooled Air Handling Unit | PAHU-2F | 2F Common Public | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (PAHU @ 2nd Level)
P0217 | Ventilation | Precooled Air Handling Unit | PAHU-2F | 2F Common Public | Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-2F | MC-ME (PAHU @ 2nd Level)
P0218 | Ventilation | Precooled Air Handling Unit | PAHU-2F | 2F Common Public | Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-2F | MC-ME (PAHU @ 2nd Level)
P0219 | Ventilation | Precooled Air Handling Unit | PAHU-2F | 2F Common Public | CHWS Coil Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-AIR-2F | MC-ME (PAHU @ 2nd Level)
P0220 | Ventilation | Precooled Air Handling Unit | PAHU-2F | 2F Common Public | CHWS Coil Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-AIR-2F | MC-ME (PAHU @ 2nd Level)
P0221 | Ventilation | Precooled Air Handling Unit | PAHU-BSMT | Basement BOH | Outdoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-BSMT | MC-ME (PAHU @ Basement)
P0222 | Ventilation | Precooled Air Handling Unit | PAHU-BSMT | Basement BOH | Outdoor Supply Air Flow | AI | Flow Sensor | BMS Contractor |  | PNL-AIR-BSMT | MC-ME (PAHU @ Basement)
P0223 | Ventilation | Precooled Air Handling Unit | PAHU-BSMT | Basement BOH | OA Damper Status | DI | Damper Controller | Equipment Supplier |  | PNL-AIR-BSMT | MC-ME (PAHU @ Basement)
P0224 | Ventilation | Precooled Air Handling Unit | PAHU-BSMT | Basement BOH | OA Damper Command | AO | Damper Controller | Equipment Supplier |  | PNL-AIR-BSMT | MC-ME (PAHU @ Basement)
P0225 | Ventilation | Precooled Air Handling Unit | PAHU-BSMT | Basement BOH | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-BSMT | MC-ME (PAHU @ Basement)
P0226 | Ventilation | Precooled Air Handling Unit | PAHU-BSMT | Basement BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-BSMT | MC-ME (PAHU @ Basement)
P0227 | Ventilation | Precooled Air Handling Unit | PAHU-BSMT | Basement BOH | Fan Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-BSMT | MC-ME (PAHU @ Basement)
P0228 | Ventilation | Precooled Air Handling Unit | PAHU-BSMT | Basement BOH | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-BSMT | MC-ME (PAHU @ Basement)
P0229 | Ventilation | Precooled Air Handling Unit | PAHU-BSMT | Basement BOH | Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-BSMT | MC-ME (PAHU @ Basement)
P0230 | Ventilation | Precooled Air Handling Unit | PAHU-BSMT | Basement BOH | Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-BSMT | MC-ME (PAHU @ Basement)
P0231 | Ventilation | Precooled Air Handling Unit | PAHU-BSMT | Basement BOH | CHWS Coil Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-AIR-BSMT | MC-ME (PAHU @ Basement)
P0232 | Ventilation | Precooled Air Handling Unit | PAHU-BSMT | Basement BOH | CHWS Coil Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-AIR-BSMT | MC-ME (PAHU @ Basement)
P0233 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0234 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0235 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0236 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0237 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | OA Damper Status | DI | Damper Controller | Equipment Supplier |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0238 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | OA Damper Command | AO | Damper Controller | Equipment Supplier |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0239 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | Return Air Damper Status | DI | Damper Controller | ME Contractor |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0240 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | Return Air Damper Command | AO | Damper Controller | ME Contractor |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0241 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0242 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0243 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0244 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0245 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0246 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-A | 2F Common Public | CHWS Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-AIR-2F | MC-ME (AHU @ 2nd Level) + BMS-02
P0247 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME + BMS-02
P0248 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME + BMS-02
P0249 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME + BMS-02
P0250 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor |  | PNL-AIR-2F | MC-ME + BMS-02
P0251 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | OA Damper Status | DI | Damper Controller | Equipment Supplier |  | PNL-AIR-2F | MC-ME + BMS-02
P0252 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | OA Damper Command | AO | Damper Controller | Equipment Supplier |  | PNL-AIR-2F | MC-ME + BMS-02
P0253 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | Return Air Damper Status | DI | Damper Controller | ME Contractor |  | PNL-AIR-2F | MC-ME + BMS-02
P0254 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | Return Air Damper Command | AO | Damper Controller | ME Contractor |  | PNL-AIR-2F | MC-ME + BMS-02
P0255 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME + BMS-02
P0256 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME + BMS-02
P0257 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-2F | MC-ME + BMS-02
P0258 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-2F | MC-ME + BMS-02
P0259 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-AIR-2F | MC-ME + BMS-02
P0260 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-2F-B | 2F Common Public | CHWS Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-AIR-2F | MC-ME + BMS-02
P0261 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0262 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0263 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0264 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0265 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | OA Damper Status | DI | Damper Controller | Equipment Supplier |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0266 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | OA Damper Command | AO | Damper Controller | Equipment Supplier |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0267 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | Return Air Damper Status | DI | Damper Controller | ME Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0268 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | Return Air Damper Command | AO | Damper Controller | ME Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0269 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0270 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0271 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0272 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0273 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0274 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-LOB | Ground Floor Lobby | CHWS Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0275 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0276 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0277 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0278 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0279 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | OA Damper Status | DI | Damper Controller | Equipment Supplier |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0280 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | OA Damper Command | AO | Damper Controller | Equipment Supplier |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0281 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | Return Air Damper Status | DI | Damper Controller | ME Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0282 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | Return Air Damper Command | AO | Damper Controller | ME Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0283 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0284 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0285 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0286 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0287 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0288 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-GF-REST | Ground Floor Restaurant | CHWS Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-AIR-GF | MC-ME (AHU @ GF)
P0289 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0290 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0291 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | Indoor Return Air CO/CO2 | AI | CO/CO2 Sensor | BMS Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0292 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | OA Damper Position Feedback | AI | Damper Controller | Equipment Supplier |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0293 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | OA Damper Modulating Command | AO | Damper Controller | Equipment Supplier |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0294 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | Return Damper Position Feedback | AI | Damper Controller | ME Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0295 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | Return Damper Modulating Command | AO | Damper Controller | ME Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0296 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0297 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0298 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0299 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0300 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | CHWS Modulating Valve Position Feedback | AI | Electric Valve Actuator | ME Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0301 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | CHWS Modulating Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0302 | Air Conditioning | AHU (Modulating CHW-served) | AHU-GF-CASINO | Ground Floor Casino Lobby | Ozone VOC Reading | AI | VOC Sensor | BMS Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS) + MC-ME
P0303 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0304 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0305 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | Indoor Return Air CO/CO2 | AI | CO/CO2 Sensor | BMS Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0306 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | OA Damper Position Feedback | AI | Damper Controller | Equipment Supplier |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0307 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | OA Damper Modulating Command | AO | Damper Controller | Equipment Supplier |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0308 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | Return Damper Position Feedback | AI | Damper Controller | ME Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0309 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | Return Damper Modulating Command | AO | Damper Controller | ME Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0310 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0311 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0312 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0313 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0314 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | CHWS Modulating Valve Position Feedback | AI | Electric Valve Actuator | ME Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0315 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | CHWS Modulating Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0316 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-1 | Ground Floor Casino | Ozone VOC Reading | AI | VOC Sensor | BMS Contractor |  | PNL-CASINO-GF | BMS-02 (Casino BMS Equipment I/O Tabulation)
P0317 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CASINO-GF | BMS-02
P0318 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-CASINO-GF | BMS-02
P0319 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | Indoor Return Air CO/CO2 | AI | CO/CO2 Sensor | BMS Contractor |  | PNL-CASINO-GF | BMS-02
P0320 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | OA Damper Position Feedback | AI | Damper Controller | Equipment Supplier |  | PNL-CASINO-GF | BMS-02
P0321 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | OA Damper Modulating Command | AO | Damper Controller | Equipment Supplier |  | PNL-CASINO-GF | BMS-02
P0322 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | Return Damper Position Feedback | AI | Damper Controller | ME Contractor |  | PNL-CASINO-GF | BMS-02
P0323 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | Return Damper Modulating Command | AO | Damper Controller | ME Contractor |  | PNL-CASINO-GF | BMS-02
P0324 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CASINO-GF | BMS-02
P0325 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CASINO-GF | BMS-02
P0326 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-CASINO-GF | BMS-02
P0327 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-CASINO-GF | BMS-02
P0328 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | CHWS Modulating Valve Position Feedback | AI | Electric Valve Actuator | ME Contractor |  | PNL-CASINO-GF | BMS-02
P0329 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | CHWS Modulating Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-CASINO-GF | BMS-02
P0330 | Casino Air Conditioning | AHU (Modulating CHW-served) | AHU-CASINO-2 | Ground Floor Casino | Ozone VOC Reading | AI | VOC Sensor | BMS Contractor |  | PNL-CASINO-GF | BMS-02
P0331 | Casino Air Conditioning | Ozone Generator (UV-light or Corona) | OZ-CASINO-1 | Ground Floor Casino | Ozone Generator Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CASINO-GF | BMS-02
P0332 | Casino Air Conditioning | Ozone Generator (UV-light or Corona) | OZ-CASINO-1 | Ground Floor Casino | Ozone Generator Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-CASINO-GF | BMS-02
P0333 | Casino Air Conditioning | Ozone Generator (UV-light or Corona) | OZ-CASINO-1 | Ground Floor Casino | Ozone Generator Start/Stop | DO | Auxiliary Contact | Equipment Supplier |  | PNL-CASINO-GF | BMS-02
P0334 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | Indoor Supply Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-3F | MC-ME (3F amenity)
P0335 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | Indoor Mixed Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-3F | MC-ME (3F amenity)
P0336 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | Indoor Return Air Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-3F | MC-ME (3F amenity)
P0337 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | Indoor Return Air CO2 | AI | CO2 Sensor | BMS Contractor |  | PNL-AIR-3F | MC-ME (3F amenity)
P0338 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | OA Damper Status | DI | Damper Controller | Equipment Supplier |  | PNL-AIR-3F | MC-ME (3F amenity)
P0339 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | OA Damper Command | AO | Damper Controller | Equipment Supplier |  | PNL-AIR-3F | MC-ME (3F amenity)
P0340 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | Return Air Damper Status | DI | Damper Controller | ME Contractor |  | PNL-AIR-3F | MC-ME (3F amenity)
P0341 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | Return Air Damper Command | AO | Damper Controller | ME Contractor |  | PNL-AIR-3F | MC-ME (3F amenity)
P0342 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-3F | MC-ME (3F amenity)
P0343 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-3F | MC-ME (3F amenity)
P0344 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | Fan VFD Speed | AI | VFD | Equipment Supplier |  | PNL-AIR-3F | MC-ME (3F amenity)
P0345 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | Fan VFD Command | AO | VFD | Equipment Supplier |  | PNL-AIR-3F | MC-ME (3F amenity)
P0346 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | CHWS Valve Status | DI | Electric Valve Actuator | ME Contractor |  | PNL-AIR-3F | MC-ME (3F amenity)
P0347 | Air Conditioning | AHU (Chilled-Water-Served) | AHU-3F-AM | 3F Amenity | CHWS Valve Command | AO | Electric Valve Actuator | ME Contractor |  | PNL-AIR-3F | MC-ME (3F amenity)
P0348 | Exhaust | Exhaust Fan (Toilet) | EAS-TOILET-BSMT | Basement BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-BSMT | BMS-01 (Basement toilet exhaust)
P0349 | Exhaust | Exhaust Fan (Toilet) | EAS-TOILET-BSMT | Basement BOH | Fan Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-BSMT | BMS-01 (Basement toilet exhaust)
P0350 | Exhaust | Exhaust Fan (Toilet) | EAS-TOILET-BSMT | Basement BOH | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-BSMT | BMS-01 (Basement toilet exhaust)
P0351 | Exhaust | Exhaust Fan (General) | EAS-GEN-BSMT | Basement BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-BSMT | BMS-01
P0352 | Exhaust | Exhaust Fan (General) | EAS-GEN-BSMT | Basement BOH | Fan Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-BSMT | BMS-01
P0353 | Exhaust | Exhaust Fan (General) | EAS-GEN-BSMT | Basement BOH | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-BSMT | BMS-01
P0354 | Exhaust | Exhaust Fan (Toilet) | EAS-TOILET-GF | Ground Floor Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-GF | MC-ME (GF main lobby toilet exhaust)
P0355 | Exhaust | Exhaust Fan (Toilet) | EAS-TOILET-GF | Ground Floor Lobby | Fan Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-GF | MC-ME (GF main lobby toilet exhaust)
P0356 | Exhaust | Exhaust Fan (Toilet) | EAS-TOILET-GF | Ground Floor Lobby | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-GF | MC-ME (GF main lobby toilet exhaust)
P0357 | Exhaust | Exhaust Fan (General) | EAS-GEN-GF | Ground Floor Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-GF | MC-ME
P0358 | Exhaust | Exhaust Fan (General) | EAS-GEN-GF | Ground Floor Lobby | Fan Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-GF | MC-ME
P0359 | Exhaust | Exhaust Fan (General) | EAS-GEN-GF | Ground Floor Lobby | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-GF | MC-ME
P0360 | Exhaust | Exhaust Fan (Toilet) | EAS-TOILET-2F | 2F Common Public | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (2nd Floor toilet exhaust)
P0361 | Exhaust | Exhaust Fan (Toilet) | EAS-TOILET-2F | 2F Common Public | Fan Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (2nd Floor toilet exhaust)
P0362 | Exhaust | Exhaust Fan (Toilet) | EAS-TOILET-2F | 2F Common Public | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME (2nd Floor toilet exhaust)
P0363 | Exhaust | Exhaust Fan (General) | EAS-GEN-2F | 2F Common Public | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME
P0364 | Exhaust | Exhaust Fan (General) | EAS-GEN-2F | 2F Common Public | Fan Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME
P0365 | Exhaust | Exhaust Fan (General) | EAS-GEN-2F | 2F Common Public | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-2F | MC-ME
P0366 | Exhaust | Exhaust Fan (Toilet) | EAS-TOILET-3F | 3F Amenity | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-3F | MC-ME (3F amenity toilet exhaust)
P0367 | Exhaust | Exhaust Fan (Toilet) | EAS-TOILET-3F | 3F Amenity | Fan Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-3F | MC-ME (3F amenity toilet exhaust)
P0368 | Exhaust | Exhaust Fan (Toilet) | EAS-TOILET-3F | 3F Amenity | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-3F | MC-ME (3F amenity toilet exhaust)
P0369 | Exhaust | Exhaust Fan (General) | EAS-GEN-3F | 3F Amenity | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-3F | MC-ME
P0370 | Exhaust | Exhaust Fan (General) | EAS-GEN-3F | 3F Amenity | Fan Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-3F | MC-ME
P0371 | Exhaust | Exhaust Fan (General) | EAS-GEN-3F | 3F Amenity | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-3F | MC-ME
P0372 | Exhaust | Exhaust Fan (General) | EAS-GEN-ROOF | Roofdeck DOAS | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (Roofdeck general exhaust)
P0373 | Exhaust | Exhaust Fan (General) | EAS-GEN-ROOF | Roofdeck DOAS | Fan Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (Roofdeck general exhaust)
P0374 | Exhaust | Exhaust Fan (General) | EAS-GEN-ROOF | Roofdeck DOAS | Fan Motor Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-ME (Roofdeck general exhaust)
P0375 | Hot Water | Calorifier (Hot Water Storage Tank) | CALOR-LG | Lower Ground Calorifier Room | Tank Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-PL-LG | MC-PL (Calorifiers @ Lower Ground)
P0376 | Hot Water | Calorifier (Hot Water Storage Tank) | CALOR-ROOF | Roofdeck DOAS | Tank Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-AIR-ROOF | MC-PL (Calorifiers @ Roofdeck)
P0377 | Hot Water | Hot Water Header Set | HW-HEADERS-LG | Lower Ground Calorifier Room | HW Supply Header Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-PL-LG | MC-PL (Supply & Return Headers @ Lower Ground)
P0378 | Hot Water | Hot Water Header Set | HW-HEADERS-LG | Lower Ground Calorifier Room | Make-up Cold Water Header Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-PL-LG | MC-PL (Supply & Return Headers @ Lower Ground)
P0379 | Hot Water | Hot Water Header Set | HW-HEADERS-LG | Lower Ground Calorifier Room | HW Return Header Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-PL-LG | MC-PL (Supply & Return Headers @ Lower Ground)
P0380 | Hot Water | Heat Pump | HP-LG-1 | Lower Ground Calorifier Room | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-PL-LG | MC-PL (Heat Pump @ Lower Ground)
P0381 | Hot Water | Heat Pump | HP-LG-1 | Lower Ground Calorifier Room | Pump Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-PL-LG | MC-PL (Heat Pump @ Lower Ground)
P0382 | Hot Water | Heat Pump | HP-LG-1 | Lower Ground Calorifier Room | Pump Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-PL-LG | MC-PL (Heat Pump @ Lower Ground)
P0383 | Hot Water | Heat Pump | HP-ROOF-1 | Roofdeck DOAS | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-PL (Heat Pump @ Roofdeck)
P0384 | Hot Water | Heat Pump | HP-ROOF-1 | Roofdeck DOAS | Pump Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-PL (Heat Pump @ Roofdeck)
P0385 | Hot Water | Heat Pump | HP-ROOF-1 | Roofdeck DOAS | Pump Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-PL (Heat Pump @ Roofdeck)
P0386 | Hot Water | Recirculating Pump | HW-PUMP-LG-1 | Lower Ground Calorifier Room | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-PL-LG | MC-PL (Circulating Pumps @ Lower Ground)
P0387 | Hot Water | Recirculating Pump | HW-PUMP-LG-1 | Lower Ground Calorifier Room | Pump Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-PL-LG | MC-PL (Circulating Pumps @ Lower Ground)
P0388 | Hot Water | Recirculating Pump | HW-PUMP-LG-1 | Lower Ground Calorifier Room | Pump Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-PL-LG | MC-PL (Circulating Pumps @ Lower Ground)
P0389 | Hot Water | Recirculating Pump | HW-PUMP-LG-2 | Lower Ground Calorifier Room | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-PL-LG | MC-PL
P0390 | Hot Water | Recirculating Pump | HW-PUMP-LG-2 | Lower Ground Calorifier Room | Pump Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-PL-LG | MC-PL
P0391 | Hot Water | Recirculating Pump | HW-PUMP-LG-2 | Lower Ground Calorifier Room | Pump Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-PL-LG | MC-PL
P0392 | Hot Water | Recirculating Pump | HW-PUMP-ROOF-1 | Roofdeck DOAS | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-PL (Roofdeck circulating pumps)
P0393 | Hot Water | Recirculating Pump | HW-PUMP-ROOF-1 | Roofdeck DOAS | Pump Motor HOA | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-PL (Roofdeck circulating pumps)
P0394 | Hot Water | Recirculating Pump | HW-PUMP-ROOF-1 | Roofdeck DOAS | Pump Trip | DI | Auxiliary Contact | Equipment Supplier |  | PNL-AIR-ROOF | MC-PL (Roofdeck circulating pumps)
P0395 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Supply Steam Pressure | AI | Pressure Sensor | BMS Contractor |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0396 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Feedwater Supply Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0397 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Fluegas Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0398 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Fluegas Oxygen Level | AI | Oxygen Sensor | BMS Contractor |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0399 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Boiler Water Low Level | DI | Level Sensor | Equipment Supplier |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0400 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Boiler Water High Level | DI | Level Sensor | Equipment Supplier |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0401 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Burner Power | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0402 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Small Fire Control Signal | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0403 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Big Fire Control Signal | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0404 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Waterfeed Pump Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0405 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Burner Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0406 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Burner Fire Running Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0407 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Blower Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0408 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Fuel Oil Pump Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0409 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Motorized Blowdown Valve Status | DI | Electric Valve Actuator | BMS Contractor |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0410 | Boiler | Steam Boiler | BLR-1 | Lower Ground Boiler Room | Motorized Blowdown Valve Command | DO | Electric Valve Actuator | BMS Contractor |  | PNL-BLR-LG | BMS-01 (Boilers @ Lower Ground) + MC-ME
P0411 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Supply Steam Pressure | AI | Pressure Sensor | BMS Contractor |  | PNL-BLR-LG | BMS-01 + MC-ME
P0412 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Feedwater Supply Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-BLR-LG | BMS-01 + MC-ME
P0413 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Fluegas Temperature | AI | Temperature Sensor | BMS Contractor |  | PNL-BLR-LG | BMS-01 + MC-ME
P0414 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Fluegas Oxygen Level | AI | Oxygen Sensor | BMS Contractor |  | PNL-BLR-LG | BMS-01 + MC-ME
P0415 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Boiler Water Low Level | DI | Level Sensor | Equipment Supplier |  | PNL-BLR-LG | BMS-01 + MC-ME
P0416 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Boiler Water High Level | DI | Level Sensor | Equipment Supplier |  | PNL-BLR-LG | BMS-01 + MC-ME
P0417 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Burner Power | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 + MC-ME
P0418 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Small Fire Control Signal | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 + MC-ME
P0419 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Big Fire Control Signal | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 + MC-ME
P0420 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Waterfeed Pump Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 + MC-ME
P0421 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Burner Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 + MC-ME
P0422 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Burner Fire Running Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 + MC-ME
P0423 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Blower Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 + MC-ME
P0424 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Fuel Oil Pump Status | DI | Auxiliary Contact | Equipment Supplier |  | PNL-BLR-LG | BMS-01 + MC-ME
P0425 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Motorized Blowdown Valve Status | DI | Electric Valve Actuator | BMS Contractor |  | PNL-BLR-LG | BMS-01 + MC-ME
P0426 | Boiler | Steam Boiler | BLR-2 | Lower Ground Boiler Room | Motorized Blowdown Valve Command | DO | Electric Valve Actuator | BMS Contractor |  | PNL-BLR-LG | BMS-01 + MC-ME
P0427 | Power Monitoring | Multifunction Power Meter (Main) | PM-MAIN-LG | Lower Ground Main Switchgear | Power Meter Modbus Network | Network | Modbus Power Meter | BMS Contractor |  | PNL-PM-LG | EE-21 (main service entry) + BMS-01 spec
P0428 | Power Monitoring | Multifunction Power Meter (Main) | PM-MAIN-LG | Lower Ground Main Switchgear | Voltage L-L (3-phase) | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PM-LG | EE-21 (main service entry) + BMS-01 spec
P0429 | Power Monitoring | Multifunction Power Meter (Main) | PM-MAIN-LG | Lower Ground Main Switchgear | Current per phase | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PM-LG | EE-21 (main service entry) + BMS-01 spec
P0430 | Power Monitoring | Multifunction Power Meter (Main) | PM-MAIN-LG | Lower Ground Main Switchgear | Real Power kW | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PM-LG | EE-21 (main service entry) + BMS-01 spec
P0431 | Power Monitoring | Multifunction Power Meter (Main) | PM-MAIN-LG | Lower Ground Main Switchgear | Reactive Power kVAR | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PM-LG | EE-21 (main service entry) + BMS-01 spec
P0432 | Power Monitoring | Multifunction Power Meter (Main) | PM-MAIN-LG | Lower Ground Main Switchgear | Power Factor | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PM-LG | EE-21 (main service entry) + BMS-01 spec
P0433 | Power Monitoring | Multifunction Power Meter (Main) | PM-MAIN-LG | Lower Ground Main Switchgear | Energy kWh | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PM-LG | EE-21 (main service entry) + BMS-01 spec
P0434 | Power Monitoring | Multifunction Power Meter (Main) | PM-MAIN-LG | Lower Ground Main Switchgear | Frequency Hz | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PM-LG | EE-21 (main service entry) + BMS-01 spec
P0435 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-CHILLER | 2F Chiller Plant Room | Power Meter Modbus Network | Network | Modbus Power Meter | BMS Contractor |  | PNL-CH-PLANT-2F | EE-21 + BMS-01 (chiller feeders)
P0436 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-CHILLER | 2F Chiller Plant Room | Voltage L-L (3-phase) | HLI | Modbus Power Meter | BMS Contractor |  | PNL-CH-PLANT-2F | EE-21 + BMS-01 (chiller feeders)
P0437 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-CHILLER | 2F Chiller Plant Room | Current per phase | HLI | Modbus Power Meter | BMS Contractor |  | PNL-CH-PLANT-2F | EE-21 + BMS-01 (chiller feeders)
P0438 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-CHILLER | 2F Chiller Plant Room | Real Power kW | HLI | Modbus Power Meter | BMS Contractor |  | PNL-CH-PLANT-2F | EE-21 + BMS-01 (chiller feeders)
P0439 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-CHILLER | 2F Chiller Plant Room | Energy kWh | HLI | Modbus Power Meter | BMS Contractor |  | PNL-CH-PLANT-2F | EE-21 + BMS-01 (chiller feeders)
P0440 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-COOLING | Roofdeck Cooling Tower | Power Meter Modbus Network | Network | Modbus Power Meter | BMS Contractor |  | PNL-CT-ROOF | EE-22 + BMS-01
P0441 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-COOLING | Roofdeck Cooling Tower | Voltage L-L (3-phase) | HLI | Modbus Power Meter | BMS Contractor |  | PNL-CT-ROOF | EE-22 + BMS-01
P0442 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-COOLING | Roofdeck Cooling Tower | Current per phase | HLI | Modbus Power Meter | BMS Contractor |  | PNL-CT-ROOF | EE-22 + BMS-01
P0443 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-COOLING | Roofdeck Cooling Tower | Real Power kW | HLI | Modbus Power Meter | BMS Contractor |  | PNL-CT-ROOF | EE-22 + BMS-01
P0444 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-COOLING | Roofdeck Cooling Tower | Energy kWh | HLI | Modbus Power Meter | BMS Contractor |  | PNL-CT-ROOF | EE-22 + BMS-01
P0445 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-AIR-2F | 2F Common Public | Power Meter Modbus Network | Network | Modbus Power Meter | BMS Contractor |  | PNL-AIR-2F | EE-22
P0446 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-AIR-2F | 2F Common Public | Voltage L-L (3-phase) | HLI | Modbus Power Meter | BMS Contractor |  | PNL-AIR-2F | EE-22
P0447 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-AIR-2F | 2F Common Public | Current per phase | HLI | Modbus Power Meter | BMS Contractor |  | PNL-AIR-2F | EE-22
P0448 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-AIR-2F | 2F Common Public | Real Power kW | HLI | Modbus Power Meter | BMS Contractor |  | PNL-AIR-2F | EE-22
P0449 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-AIR-2F | 2F Common Public | Energy kWh | HLI | Modbus Power Meter | BMS Contractor |  | PNL-AIR-2F | EE-22
P0450 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-AIR-GF | Ground Floor Lobby | Power Meter Modbus Network | Network | Modbus Power Meter | BMS Contractor |  | PNL-AIR-GF | EE-22
P0451 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-AIR-GF | Ground Floor Lobby | Voltage L-L (3-phase) | HLI | Modbus Power Meter | BMS Contractor |  | PNL-AIR-GF | EE-22
P0452 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-AIR-GF | Ground Floor Lobby | Current per phase | HLI | Modbus Power Meter | BMS Contractor |  | PNL-AIR-GF | EE-22
P0453 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-AIR-GF | Ground Floor Lobby | Real Power kW | HLI | Modbus Power Meter | BMS Contractor |  | PNL-AIR-GF | EE-22
P0454 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-AIR-GF | Ground Floor Lobby | Energy kWh | HLI | Modbus Power Meter | BMS Contractor |  | PNL-AIR-GF | EE-22
P0455 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-CASINO | Ground Floor Casino | Power Meter Modbus Network | Network | Modbus Power Meter | BMS Contractor |  | PNL-CASINO-GF | EE-22 (Casino feeder)
P0456 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-CASINO | Ground Floor Casino | Voltage L-L (3-phase) | HLI | Modbus Power Meter | BMS Contractor |  | PNL-CASINO-GF | EE-22 (Casino feeder)
P0457 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-CASINO | Ground Floor Casino | Current per phase | HLI | Modbus Power Meter | BMS Contractor |  | PNL-CASINO-GF | EE-22 (Casino feeder)
P0458 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-CASINO | Ground Floor Casino | Real Power kW | HLI | Modbus Power Meter | BMS Contractor |  | PNL-CASINO-GF | EE-22 (Casino feeder)
P0459 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-CASINO | Ground Floor Casino | Energy kWh | HLI | Modbus Power Meter | BMS Contractor |  | PNL-CASINO-GF | EE-22 (Casino feeder)
P0460 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-BOILER | Lower Ground Boiler Room | Power Meter Modbus Network | Network | Modbus Power Meter | BMS Contractor |  | PNL-BLR-LG | EE-23 (boiler feeder)
P0461 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-BOILER | Lower Ground Boiler Room | Voltage L-L (3-phase) | HLI | Modbus Power Meter | BMS Contractor |  | PNL-BLR-LG | EE-23 (boiler feeder)
P0462 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-BOILER | Lower Ground Boiler Room | Current per phase | HLI | Modbus Power Meter | BMS Contractor |  | PNL-BLR-LG | EE-23 (boiler feeder)
P0463 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-BOILER | Lower Ground Boiler Room | Real Power kW | HLI | Modbus Power Meter | BMS Contractor |  | PNL-BLR-LG | EE-23 (boiler feeder)
P0464 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-BOILER | Lower Ground Boiler Room | Energy kWh | HLI | Modbus Power Meter | BMS Contractor |  | PNL-BLR-LG | EE-23 (boiler feeder)
P0465 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-PLUMB | Lower Ground Calorifier Room | Power Meter Modbus Network | Network | Modbus Power Meter | BMS Contractor |  | PNL-PL-LG | EE-23 (plumbing pumproom feeder)
P0466 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-PLUMB | Lower Ground Calorifier Room | Voltage L-L (3-phase) | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PL-LG | EE-23 (plumbing pumproom feeder)
P0467 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-PLUMB | Lower Ground Calorifier Room | Current per phase | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PL-LG | EE-23 (plumbing pumproom feeder)
P0468 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-PLUMB | Lower Ground Calorifier Room | Real Power kW | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PL-LG | EE-23 (plumbing pumproom feeder)
P0469 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-PLUMB | Lower Ground Calorifier Room | Energy kWh | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PL-LG | EE-23 (plumbing pumproom feeder)
P0470 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-FIREPMP | Lower Ground Boiler Room | Power Meter Modbus Network | Network | Modbus Power Meter | BMS Contractor |  | PNL-PL-LG | EE-23 (fire pump feeder per CB#8 — single-feeder scheme)
P0471 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-FIREPMP | Lower Ground Boiler Room | Voltage L-L (3-phase) | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PL-LG | EE-23 (fire pump feeder per CB#8 — single-feeder scheme)
P0472 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-FIREPMP | Lower Ground Boiler Room | Current per phase | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PL-LG | EE-23 (fire pump feeder per CB#8 — single-feeder scheme)
P0473 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-FIREPMP | Lower Ground Boiler Room | Real Power kW | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PL-LG | EE-23 (fire pump feeder per CB#8 — single-feeder scheme)
P0474 | Power Monitoring | Multifunction Power Meter (Feeder) | PM-FIREPMP | Lower Ground Boiler Room | Energy kWh | HLI | Modbus Power Meter | BMS Contractor |  | PNL-PL-LG | EE-23 (fire pump feeder per CB#8 — single-feeder scheme)