## Summary
A2 — Equipment Takeoff Summary
Total instances | 59
By equipment class
Multifunction Power Meter (Feeder) | 8
AHU (Chilled-Water-Served) | 5
Exhaust Fan (General) | 5
Exhaust Fan (Toilet) | 4
AHU (Modulating CHW-served) | 3
Condenser Water Pump | 3
DOAS Unit | 3
Recirculating Pump | 3
Precooled Air Handling Unit | 3
Steam Boiler | 2
Calorifier (Hot Water Storage Tank) | 2
Chiller (Package Water-Cooled) | 2
Primary CHW Pump | 2
Cooling Tower | 2
Heat Pump | 2
BTU Meter | 1
CHW Bypass Header | 1
CHW Return Main Header | 1
CHW Supply Main Header | 1
Primary CHW Pump (Standby) | 1
Cooling Tower (Common) | 1
Condenser Water Header | 1
Hot Water Header Set | 1
Ozone Generator (UV-light or Corona) | 1
Multifunction Power Meter (Main) | 1
By location
2F Chiller Plant Room | 13
2F Common Public | 7
Roofdeck DOAS | 7
Lower Ground Calorifier Room | 6
Roofdeck Cooling Tower | 5
Ground Floor Casino | 4
Ground Floor Lobby | 4
Lower Ground Boiler Room | 4
3F Amenity | 3
Basement BOH | 3
Ground Floor Casino Lobby | 1
Ground Floor Restaurant | 1
Lower Ground Main Switchgear | 1
By panel
PNL-CH-PLANT-2F | 13
PNL-AIR-2F | 7
PNL-PL-LG | 7
PNL-AIR-ROOF | 7
PNL-CASINO-GF | 5
PNL-AIR-GF | 5
PNL-CT-ROOF | 5
PNL-AIR-3F | 3
PNL-BLR-LG | 3
PNL-AIR-BSMT | 3
PNL-PM-LG | 1

## Equipment Takeoff
ID | Equipment Class | Quantity | Location | System | Panel | Primary C/O | Physical I/O | HLI Subpoints | Network Drops | Total I/O | Make/Model Assumed | Network Type | Typical Supplier | Notes
AHU-2F-A | AHU (Chilled-Water-Served) | 1 | 2F Common Public | Air Conditioning | PNL-AIR-2F | Equipment Supplier | 14 | 0 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-2F-B | AHU (Chilled-Water-Served) | 1 | 2F Common Public | Air Conditioning | PNL-AIR-2F | Equipment Supplier | 14 | 0 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-3F-AM | AHU (Chilled-Water-Served) | 1 | 3F Amenity | Air Conditioning | PNL-AIR-3F | Equipment Supplier | 14 | 0 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-CASINO-1 | AHU (Modulating CHW-served) | 1 | Ground Floor Casino | Casino Air Conditioning | PNL-CASINO-GF | Equipment Supplier | 14 | 0 | 0 | 14 | Modulating CHW-served AHU with VFD, modulating valve and dampers (position feedback) | Hardwired (VFD via BACnet HLI) | Mechanical contractor | Casino-spec AHU — modulating actuators with position feedback; CO/CO2 monitoring at return duct.
AHU-CASINO-2 | AHU (Modulating CHW-served) | 1 | Ground Floor Casino | Casino Air Conditioning | PNL-CASINO-GF | Equipment Supplier | 14 | 0 | 0 | 14 | Modulating CHW-served AHU with VFD, modulating valve and dampers (position feedback) | Hardwired (VFD via BACnet HLI) | Mechanical contractor | Casino-spec AHU — modulating actuators with position feedback; CO/CO2 monitoring at return duct.
AHU-GF-CASINO | AHU (Modulating CHW-served) | 1 | Ground Floor Casino Lobby | Air Conditioning | PNL-CASINO-GF | Equipment Supplier | 14 | 0 | 0 | 14 | Modulating CHW-served AHU with VFD, modulating valve and dampers (position feedback) | Hardwired (VFD via BACnet HLI) | Mechanical contractor | Casino-spec AHU — modulating actuators with position feedback; CO/CO2 monitoring at return duct.
AHU-GF-LOB | AHU (Chilled-Water-Served) | 1 | Ground Floor Lobby | Air Conditioning | PNL-AIR-GF | Equipment Supplier | 14 | 0 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-GF-REST | AHU (Chilled-Water-Served) | 1 | Ground Floor Restaurant | Air Conditioning | PNL-AIR-GF | Equipment Supplier | 14 | 0 | 0 | 14 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
BLR-1 | Steam Boiler | 1 | Lower Ground Boiler Room | Boiler | PNL-BLR-LG | Equipment Supplier | 16 | 0 | 0 | 16 | Fire-tube steam boiler with multi-stage burner, fuel-oil fired (typical for hotel laundry) | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies steam pressure, feedwater T, fluegas T+O2 sensors. Boiler equipment provides aux contacts for status/HOA/trip points.
BLR-2 | Steam Boiler | 1 | Lower Ground Boiler Room | Boiler | PNL-BLR-LG | Equipment Supplier | 16 | 0 | 0 | 16 | Fire-tube steam boiler with multi-stage burner, fuel-oil fired (typical for hotel laundry) | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies steam pressure, feedwater T, fluegas T+O2 sensors. Boiler equipment provides aux contacts for status/HOA/trip points.
BTU-CHW-MAIN | BTU Meter | 1 | 2F Chiller Plant Room | Chilled Water Plant | PNL-CH-PLANT-2F | BMS Contractor | 0 | 4 | 1 | 5 | Ultrasonic or insertion-type BTU meter with Modbus output (Onicon, Aichi, Kamstrup) | Modbus RTU/TCP | BMS contractor | System-level energy submeter.
CALOR-LG | Calorifier (Hot Water Storage Tank) | 1 | Lower Ground Calorifier Room | Hot Water | PNL-PL-LG | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
CALOR-ROOF | Calorifier (Hot Water Storage Tank) | 1 | Roofdeck DOAS | Hot Water | PNL-AIR-ROOF | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
CH-1 | Chiller (Package Water-Cooled) | 1 | 2F Chiller Plant Room | Chilled Water Plant | PNL-CH-PLANT-2F | Equipment Supplier | 9 | 18 | 1 | 28 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CH-2 | Chiller (Package Water-Cooled) | 1 | 2F Chiller Plant Room | Chilled Water Plant | PNL-CH-PLANT-2F | Equipment Supplier | 9 | 18 | 1 | 28 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CHW-BYP | CHW Bypass Header | 1 | 2F Chiller Plant Room | Chilled Water Plant | PNL-CH-PLANT-2F | BMS Contractor | 4 | 0 | 0 | 4 | BMS dP/dT sensors + motorized bypass valve (BMS-supplied) | Hardwired | BMS contractor | BMS controls bypass valve to maintain CHW differential.
CHW-RET-HDR | CHW Return Main Header | 1 | 2F Chiller Plant Room | Chilled Water Plant | PNL-CH-PLANT-2F | BMS Contractor | 2 | 0 | 0 | 2 | BMS T+P sensors on CHW return manifold | Hardwired | BMS contractor | Field instrumentation only.
CHW-SUP-HDR | CHW Supply Main Header | 1 | 2F Chiller Plant Room | Chilled Water Plant | PNL-CH-PLANT-2F | BMS Contractor | 2 | 0 | 0 | 2 | BMS T+P sensors on CHW supply manifold | Hardwired | BMS contractor | Field instrumentation only.
CHWP-1 | Primary CHW Pump | 1 | 2F Chiller Plant Room | Chilled Water Plant | PNL-CH-PLANT-2F | Equipment Supplier | 7 | 0 | 0 | 7 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
CHWP-2 | Primary CHW Pump | 1 | 2F Chiller Plant Room | Chilled Water Plant | PNL-CH-PLANT-2F | Equipment Supplier | 7 | 0 | 0 | 7 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
CHWP-3 | Primary CHW Pump (Standby) | 1 | 2F Chiller Plant Room | Chilled Water Plant | PNL-CH-PLANT-2F | Equipment Supplier | 7 | 0 | 0 | 7 | Same as Primary CHW Pump (1 standby for N+1 redundancy) | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | Standby unit per A-CHW-001.
CT-1 | Cooling Tower | 1 | Roofdeck Cooling Tower | Condenser Water Loop | PNL-CT-ROOF | BMS Contractor | 7 | 0 | 0 | 7 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-2 | Cooling Tower | 1 | Roofdeck Cooling Tower | Condenser Water Loop | PNL-CT-ROOF | BMS Contractor | 7 | 0 | 0 | 7 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-COMMON | Cooling Tower (Common) | 1 | Roofdeck Cooling Tower | Condenser Water Loop | PNL-CT-ROOF | BMS Contractor | 6 | 0 | 0 | 6 | Common BMS sensors at cooling tower area (OA T/RH, condenser headers) | Hardwired | BMS contractor | Field instrumentation only — no equipment per se.
CW-HDR | Condenser Water Header | 1 | Roofdeck Cooling Tower | Condenser Water Loop | PNL-CT-ROOF | BMS Contractor | 2 | 0 | 0 | 2 | BMS T sensors on condenser water headers at roofdeck | Hardwired | BMS contractor | Field instrumentation only.
CWP-1 | Condenser Water Pump | 1 | 2F Chiller Plant Room | Condenser Water Loop | PNL-CH-PLANT-2F | Equipment Supplier | 4 | 0 | 0 | 4 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
CWP-2 | Condenser Water Pump | 1 | 2F Chiller Plant Room | Condenser Water Loop | PNL-CH-PLANT-2F | Equipment Supplier | 4 | 0 | 0 | 4 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
CWP-3 | Condenser Water Pump | 1 | 2F Chiller Plant Room | Condenser Water Loop | PNL-CH-PLANT-2F | Equipment Supplier | 4 | 0 | 0 | 4 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
DOAS-2F | DOAS Unit | 1 | 2F Common Public | Ventilation | PNL-AIR-2F | Equipment Supplier | 24 | 0 | 0 | 24 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
DOAS-RD1 | DOAS Unit | 1 | Roofdeck DOAS | Ventilation | PNL-AIR-ROOF | Equipment Supplier | 24 | 0 | 0 | 24 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
DOAS-RD2 | DOAS Unit | 1 | Roofdeck DOAS | Ventilation | PNL-AIR-ROOF | Equipment Supplier | 24 | 0 | 0 | 24 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
EAS-GEN-2F | Exhaust Fan (General) | 1 | 2F Common Public | Exhaust | PNL-AIR-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EAS-GEN-3F | Exhaust Fan (General) | 1 | 3F Amenity | Exhaust | PNL-AIR-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EAS-GEN-BSMT | Exhaust Fan (General) | 1 | Basement BOH | Exhaust | PNL-AIR-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EAS-GEN-GF | Exhaust Fan (General) | 1 | Ground Floor Lobby | Exhaust | PNL-AIR-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EAS-GEN-ROOF | Exhaust Fan (General) | 1 | Roofdeck DOAS | Exhaust | PNL-AIR-ROOF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EAS-TOILET-2F | Exhaust Fan (Toilet) | 1 | 2F Common Public | Exhaust | PNL-AIR-2F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EAS-TOILET-3F | Exhaust Fan (Toilet) | 1 | 3F Amenity | Exhaust | PNL-AIR-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EAS-TOILET-BSMT | Exhaust Fan (Toilet) | 1 | Basement BOH | Exhaust | PNL-AIR-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EAS-TOILET-GF | Exhaust Fan (Toilet) | 1 | Ground Floor Lobby | Exhaust | PNL-AIR-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
HP-LG-1 | Heat Pump | 1 | Lower Ground Calorifier Room | Hot Water | PNL-PL-LG | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-ROOF-1 | Heat Pump | 1 | Roofdeck DOAS | Hot Water | PNL-AIR-ROOF | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HW-HEADERS-LG | Hot Water Header Set | 1 | Lower Ground Calorifier Room | Hot Water | PNL-PL-LG | BMS Contractor | 3 | 0 | 0 | 3 | Hot water supply/return manifolds with BMS T sensors and make-up cold water T sensor | Hardwired | BMS contractor | Field instrumentation on existing piping.
HW-PUMP-LG-1 | Recirculating Pump | 1 | Lower Ground Calorifier Room | Hot Water | PNL-PL-LG | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
HW-PUMP-LG-2 | Recirculating Pump | 1 | Lower Ground Calorifier Room | Hot Water | PNL-PL-LG | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
HW-PUMP-ROOF-1 | Recirculating Pump | 1 | Roofdeck DOAS | Hot Water | PNL-AIR-ROOF | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
OZ-CASINO-1 | Ozone Generator (UV-light or Corona) | 1 | Ground Floor Casino | Casino Air Conditioning | PNL-CASINO-GF | Equipment Supplier | 3 | 0 | 0 | 3 | UV-light or corona-discharge ozone generator (paired with Casino AHU) | Hardwired | Equipment supplier | Casino-specific air-treatment device. BMS monitors status/trip and reads VOC sensor (BMS-supplied).
PAHU-2F | Precooled Air Handling Unit | 1 | 2F Common Public | Ventilation | PNL-AIR-2F | Equipment Supplier | 12 | 0 | 0 | 12 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-BSMT | Precooled Air Handling Unit | 1 | Basement BOH | Ventilation | PNL-AIR-BSMT | Equipment Supplier | 12 | 0 | 0 | 12 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-ROOF | Precooled Air Handling Unit | 1 | Roofdeck DOAS | Ventilation | PNL-AIR-ROOF | Equipment Supplier | 12 | 0 | 0 | 12 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PM-AIR-2F | Multifunction Power Meter (Feeder) | 1 | 2F Common Public | Power Monitoring | PNL-AIR-2F | BMS Contractor | 0 | 4 | 1 | 5 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-AIR-GF | Multifunction Power Meter (Feeder) | 1 | Ground Floor Lobby | Power Monitoring | PNL-AIR-GF | BMS Contractor | 0 | 4 | 1 | 5 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-BOILER | Multifunction Power Meter (Feeder) | 1 | Lower Ground Boiler Room | Power Monitoring | PNL-BLR-LG | BMS Contractor | 0 | 4 | 1 | 5 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-CASINO | Multifunction Power Meter (Feeder) | 1 | Ground Floor Casino | Power Monitoring | PNL-CASINO-GF | BMS Contractor | 0 | 4 | 1 | 5 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-CHILLER | Multifunction Power Meter (Feeder) | 1 | 2F Chiller Plant Room | Power Monitoring | PNL-CH-PLANT-2F | BMS Contractor | 0 | 4 | 1 | 5 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-COOLING | Multifunction Power Meter (Feeder) | 1 | Roofdeck Cooling Tower | Power Monitoring | PNL-CT-ROOF | BMS Contractor | 0 | 4 | 1 | 5 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-FIREPMP | Multifunction Power Meter (Feeder) | 1 | Lower Ground Boiler Room | Power Monitoring | PNL-PL-LG | BMS Contractor | 0 | 4 | 1 | 5 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-MAIN-LG | Multifunction Power Meter (Main) | 1 | Lower Ground Main Switchgear | Power Monitoring | PNL-PM-LG | BMS Contractor | 0 | 7 | 1 | 8 | Multifunction power meter with Modbus output (Schneider PM-series, ABB M2M, Siemens SENTRON), main switchgear class | Modbus RTU/TCP | BMS contractor | Mounted in main switchgear or on dedicated BMS-side panel.
PM-PLUMB | Multifunction Power Meter (Feeder) | 1 | Lower Ground Calorifier Room | Power Monitoring | PNL-PL-LG | BMS Contractor | 0 | 4 | 1 | 5 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.