## Summary
A3 — Cable Schedule Summary
Total field cable runs | 96
Total field cable length (m) | 1870
Total trunk cable length (m) | 730
Total power feed length (m) | 232
GRAND TOTAL cable length (m) | 2832
By cable type (m)
4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 781
4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 507
4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 384
Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 198

## Field Cables
ID | From | To | Equipment Class | System | Location | Cable Type | Conductors Required | Conductors Specified | Length (m) | I/O Points Carried | Notes
C0001 | PNL-AIR-2F | AHU-2F-A (BMS Contractor) | AHU (Chilled-Water-Served) | Air Conditioning | 2F Common Public | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0002 | PNL-AIR-2F | AHU-2F-A (Equipment Supplier) | AHU (Chilled-Water-Served) | Air Conditioning | 2F Common Public | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (typical_range:boh_same_floor_field)
C0003 | PNL-AIR-2F | AHU-2F-A (ME Contractor) | AHU (Chilled-Water-Served) | Air Conditioning | 2F Common Public | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0004 | PNL-AIR-2F | AHU-2F-B (BMS Contractor) | AHU (Chilled-Water-Served) | Air Conditioning | 2F Common Public | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0005 | PNL-AIR-2F | AHU-2F-B (Equipment Supplier) | AHU (Chilled-Water-Served) | Air Conditioning | 2F Common Public | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (typical_range:boh_same_floor_field)
C0006 | PNL-AIR-2F | AHU-2F-B (ME Contractor) | AHU (Chilled-Water-Served) | Air Conditioning | 2F Common Public | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0007 | PNL-AIR-3F | AHU-3F-AM (BMS Contractor) | AHU (Chilled-Water-Served) | Air Conditioning | 3F Amenity | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0008 | PNL-AIR-3F | AHU-3F-AM (Equipment Supplier) | AHU (Chilled-Water-Served) | Air Conditioning | 3F Amenity | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (typical_range:boh_same_floor_field)
C0009 | PNL-AIR-3F | AHU-3F-AM (ME Contractor) | AHU (Chilled-Water-Served) | Air Conditioning | 3F Amenity | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0010 | PNL-CASINO-GF | AHU-CASINO-1 (BMS Contractor) | AHU (Modulating CHW-served) | Casino Air Conditioning | Ground Floor Casino | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0011 | PNL-CASINO-GF | AHU-CASINO-1 (Equipment Supplier) | AHU (Modulating CHW-served) | Casino Air Conditioning | Ground Floor Casino | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (typical_range:boh_same_floor_field)
C0012 | PNL-CASINO-GF | AHU-CASINO-1 (ME Contractor) | AHU (Modulating CHW-served) | Casino Air Conditioning | Ground Floor Casino | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0013 | PNL-CASINO-GF | AHU-CASINO-2 (BMS Contractor) | AHU (Modulating CHW-served) | Casino Air Conditioning | Ground Floor Casino | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0014 | PNL-CASINO-GF | AHU-CASINO-2 (Equipment Supplier) | AHU (Modulating CHW-served) | Casino Air Conditioning | Ground Floor Casino | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (typical_range:boh_same_floor_field)
C0015 | PNL-CASINO-GF | AHU-CASINO-2 (ME Contractor) | AHU (Modulating CHW-served) | Casino Air Conditioning | Ground Floor Casino | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0016 | PNL-CASINO-GF | AHU-GF-CASINO (BMS Contractor) | AHU (Modulating CHW-served) | Air Conditioning | Ground Floor Casino Lobby | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0017 | PNL-CASINO-GF | AHU-GF-CASINO (Equipment Supplier) | AHU (Modulating CHW-served) | Air Conditioning | Ground Floor Casino Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (typical_range:boh_same_floor_field)
C0018 | PNL-CASINO-GF | AHU-GF-CASINO (ME Contractor) | AHU (Modulating CHW-served) | Air Conditioning | Ground Floor Casino Lobby | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0019 | PNL-AIR-GF | AHU-GF-LOB (BMS Contractor) | AHU (Chilled-Water-Served) | Air Conditioning | Ground Floor Lobby | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0020 | PNL-AIR-GF | AHU-GF-LOB (Equipment Supplier) | AHU (Chilled-Water-Served) | Air Conditioning | Ground Floor Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (typical_range:boh_same_floor_field)
C0021 | PNL-AIR-GF | AHU-GF-LOB (ME Contractor) | AHU (Chilled-Water-Served) | Air Conditioning | Ground Floor Lobby | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0022 | PNL-AIR-GF | AHU-GF-REST (BMS Contractor) | AHU (Chilled-Water-Served) | Air Conditioning | Ground Floor Restaurant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0023 | PNL-AIR-GF | AHU-GF-REST (Equipment Supplier) | AHU (Chilled-Water-Served) | Air Conditioning | Ground Floor Restaurant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (typical_range:boh_same_floor_field)
C0024 | PNL-AIR-GF | AHU-GF-REST (ME Contractor) | AHU (Chilled-Water-Served) | Air Conditioning | Ground Floor Restaurant | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0025 | PNL-BLR-LG | BLR-1 (BMS Contractor) | Steam Boiler | Boiler | Lower Ground Boiler Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 10 | 6 | 6 I/O points carried, 8C cable; length 10 m (measured)
C0026 | PNL-BLR-LG | BLR-1 (Equipment Supplier) | Steam Boiler | Boiler | Lower Ground Boiler Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | 12 | 12 | 10 | 10 I/O points carried, 12C cable; length 12 m (typical_range:plant_room_same_room)
C0027 | PNL-BLR-LG | BLR-2 (BMS Contractor) | Steam Boiler | Boiler | Lower Ground Boiler Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 12 | 6 | 6 I/O points carried, 8C cable; length 12 m (measured)
C0028 | PNL-BLR-LG | BLR-2 (Equipment Supplier) | Steam Boiler | Boiler | Lower Ground Boiler Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | 12 | 12 | 10 | 10 I/O points carried, 12C cable; length 12 m (typical_range:plant_room_same_room)
C0029 | PNL-PL-LG | CALOR-LG (BMS Contractor) | Calorifier (Hot Water Storage Tank) | Hot Water | Lower Ground Calorifier Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 8 | 1 | 1 I/O points carried, 4C cable; length 8 m (measured)
C0030 | PNL-AIR-ROOF | CALOR-ROOF (BMS Contractor) | Calorifier (Hot Water Storage Tank) | Hot Water | Roofdeck DOAS | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0031 | PNL-CH-PLANT-2F | CH-1 (BMS Contractor) | Chiller (Package Water-Cooled) | Chilled Water Plant | 2F Chiller Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 9 | 12 | 15 | 7 | 7 I/O points carried, 12C cable; length 15 m (measured)
C0032 | PNL-CH-PLANT-2F | CH-1 (ME Contractor) | Chiller (Package Water-Cooled) | Chilled Water Plant | 2F Chiller Plant Room | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0033 | PNL-CH-PLANT-2F | CH-2 (BMS Contractor) | Chiller (Package Water-Cooled) | Chilled Water Plant | 2F Chiller Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 9 | 12 | 18 | 7 | 7 I/O points carried, 12C cable; length 18 m (measured)
C0034 | PNL-CH-PLANT-2F | CH-2 (ME Contractor) | Chiller (Package Water-Cooled) | Chilled Water Plant | 2F Chiller Plant Room | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0035 | PNL-CH-PLANT-2F | CHW-BYP (BMS Contractor) | CHW Bypass Header | Chilled Water Plant | 2F Chiller Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 10 | 4 | 4 I/O points carried, 6C cable; length 10 m (measured)
C0036 | PNL-CH-PLANT-2F | CHW-RET-HDR (BMS Contractor) | CHW Return Main Header | Chilled Water Plant | 2F Chiller Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 8 | 2 | 2 I/O points carried, 4C cable; length 8 m (measured)
C0037 | PNL-CH-PLANT-2F | CHW-SUP-HDR (BMS Contractor) | CHW Supply Main Header | Chilled Water Plant | 2F Chiller Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 8 | 2 | 2 I/O points carried, 4C cable; length 8 m (measured)
C0038 | PNL-CH-PLANT-2F | CHWP-1 (Equipment Supplier) | Primary CHW Pump | Chilled Water Plant | 2F Chiller Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 9 | 12 | 10 | 7 | 7 I/O points carried, 12C cable; length 10 m (measured)
C0039 | PNL-CH-PLANT-2F | CHWP-2 (Equipment Supplier) | Primary CHW Pump | Chilled Water Plant | 2F Chiller Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 9 | 12 | 11 | 7 | 7 I/O points carried, 12C cable; length 11 m (measured)
C0040 | PNL-CH-PLANT-2F | CHWP-3 (Equipment Supplier) | Primary CHW Pump (Standby) | Chilled Water Plant | 2F Chiller Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 9 | 12 | 12 | 7 | 7 I/O points carried, 12C cable; length 12 m (measured)
C0041 | PNL-CT-ROOF | CT-1 (BMS Contractor) | Cooling Tower | Condenser Water Loop | Roofdeck Cooling Tower | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 12 | 4 | 4 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0042 | PNL-CT-ROOF | CT-1 (Equipment Supplier) | Cooling Tower | Condenser Water Loop | Roofdeck Cooling Tower | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 14 | 3 | 3 I/O points carried, 6C cable; length 14 m (measured)
C0043 | PNL-CT-ROOF | CT-2 (BMS Contractor) | Cooling Tower | Condenser Water Loop | Roofdeck Cooling Tower | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 12 | 4 | 4 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0044 | PNL-CT-ROOF | CT-2 (Equipment Supplier) | Cooling Tower | Condenser Water Loop | Roofdeck Cooling Tower | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 16 | 3 | 3 I/O points carried, 6C cable; length 16 m (measured)
C0045 | PNL-CT-ROOF | CT-COMMON (BMS Contractor) | Cooling Tower (Common) | Condenser Water Loop | Roofdeck Cooling Tower | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 12 | 4 | 4 I/O points carried, 6C cable; length 12 m (measured)
C0046 | PNL-CT-ROOF | CT-COMMON (ME Contractor) | Cooling Tower (Common) | Condenser Water Loop | Roofdeck Cooling Tower | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0047 | PNL-CT-ROOF | CW-HDR (BMS Contractor) | Condenser Water Header | Condenser Water Loop | Roofdeck Cooling Tower | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0048 | PNL-CH-PLANT-2F | CWP-1 (Equipment Supplier) | Condenser Water Pump | Condenser Water Loop | 2F Chiller Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 13 | 4 | 4 I/O points carried, 6C cable; length 13 m (measured)
C0049 | PNL-CH-PLANT-2F | CWP-2 (Equipment Supplier) | Condenser Water Pump | Condenser Water Loop | 2F Chiller Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 13 | 4 | 4 I/O points carried, 6C cable; length 13 m (measured)
C0050 | PNL-CH-PLANT-2F | CWP-3 (Equipment Supplier) | Condenser Water Pump | Condenser Water Loop | 2F Chiller Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 14 | 4 | 4 I/O points carried, 6C cable; length 14 m (measured)
C0051 | PNL-AIR-2F | DOAS-2F (BMS Contractor) | DOAS Unit | Ventilation | 2F Common Public | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (typical_range:boh_same_floor_field)
C0052 | PNL-AIR-2F | DOAS-2F (Equipment Supplier) | DOAS Unit | Ventilation | 2F Common Public | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 16 | 16 | 30 | 14 | 14 I/O points carried, 16C cable; length 30 m (typical_range:boh_same_floor_field)
C0053 | PNL-AIR-2F | DOAS-2F (ME Contractor) | DOAS Unit | Ventilation | 2F Common Public | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0054 | PNL-AIR-ROOF | DOAS-RD1 (BMS Contractor) | DOAS Unit | Ventilation | Roofdeck DOAS | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 12 | 6 | 6 I/O points carried, 8C cable; length 12 m (typical_range:plant_room_same_room)
C0055 | PNL-AIR-ROOF | DOAS-RD1 (Equipment Supplier) | DOAS Unit | Ventilation | Roofdeck DOAS | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 16 | 16 | 12 | 14 | 14 I/O points carried, 16C cable; length 12 m (typical_range:plant_room_same_room)
C0056 | PNL-AIR-ROOF | DOAS-RD1 (ME Contractor) | DOAS Unit | Ventilation | Roofdeck DOAS | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 12 | 4 | 4 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0057 | PNL-AIR-ROOF | DOAS-RD2 (BMS Contractor) | DOAS Unit | Ventilation | Roofdeck DOAS | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 12 | 6 | 6 I/O points carried, 8C cable; length 12 m (typical_range:plant_room_same_room)
C0058 | PNL-AIR-ROOF | DOAS-RD2 (Equipment Supplier) | DOAS Unit | Ventilation | Roofdeck DOAS | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 16 | 16 | 12 | 14 | 14 I/O points carried, 16C cable; length 12 m (typical_range:plant_room_same_room)
C0059 | PNL-AIR-ROOF | DOAS-RD2 (ME Contractor) | DOAS Unit | Ventilation | Roofdeck DOAS | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 12 | 4 | 4 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0060 | PNL-AIR-2F | EAS-GEN-2F (Equipment Supplier) | Exhaust Fan (General) | Exhaust | 2F Common Public | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0061 | PNL-AIR-3F | EAS-GEN-3F (Equipment Supplier) | Exhaust Fan (General) | Exhaust | 3F Amenity | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0062 | PNL-AIR-BSMT | EAS-GEN-BSMT (Equipment Supplier) | Exhaust Fan (General) | Exhaust | Basement BOH | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 12 | 3 | 3 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0063 | PNL-AIR-GF | EAS-GEN-GF (Equipment Supplier) | Exhaust Fan (General) | Exhaust | Ground Floor Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0064 | PNL-AIR-ROOF | EAS-GEN-ROOF (Equipment Supplier) | Exhaust Fan (General) | Exhaust | Roofdeck DOAS | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 12 | 3 | 3 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0065 | PNL-AIR-2F | EAS-TOILET-2F (Equipment Supplier) | Exhaust Fan (Toilet) | Exhaust | 2F Common Public | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0066 | PNL-AIR-3F | EAS-TOILET-3F (Equipment Supplier) | Exhaust Fan (Toilet) | Exhaust | 3F Amenity | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0067 | PNL-AIR-BSMT | EAS-TOILET-BSMT (Equipment Supplier) | Exhaust Fan (Toilet) | Exhaust | Basement BOH | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 12 | 3 | 3 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0068 | PNL-AIR-GF | EAS-TOILET-GF (Equipment Supplier) | Exhaust Fan (Toilet) | Exhaust | Ground Floor Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0069 | PNL-PL-LG | HP-LG-1 (Equipment Supplier) | Heat Pump | Hot Water | Lower Ground Calorifier Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 12 | 3 | 3 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0070 | PNL-AIR-ROOF | HP-ROOF-1 (Equipment Supplier) | Heat Pump | Hot Water | Roofdeck DOAS | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 12 | 3 | 3 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0071 | PNL-PL-LG | HW-HEADERS-LG (BMS Contractor) | Hot Water Header Set | Hot Water | Lower Ground Calorifier Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 10 | 3 | 3 I/O points carried, 6C cable; length 10 m (measured)
C0072 | PNL-PL-LG | HW-PUMP-LG-1 (Equipment Supplier) | Recirculating Pump | Hot Water | Lower Ground Calorifier Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 12 | 3 | 3 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0073 | PNL-PL-LG | HW-PUMP-LG-2 (Equipment Supplier) | Recirculating Pump | Hot Water | Lower Ground Calorifier Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 12 | 3 | 3 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0074 | PNL-AIR-ROOF | HW-PUMP-ROOF-1 (Equipment Supplier) | Recirculating Pump | Hot Water | Roofdeck DOAS | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 12 | 3 | 3 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0075 | PNL-CASINO-GF | OZ-CASINO-1 (Equipment Supplier) | Ozone Generator (UV-light or Corona) | Casino Air Conditioning | Ground Floor Casino | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0076 | PNL-AIR-2F | PAHU-2F (BMS Contractor) | Precooled Air Handling Unit | Ventilation | 2F Common Public | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (typical_range:boh_same_floor_field)
C0077 | PNL-AIR-2F | PAHU-2F (Equipment Supplier) | Precooled Air Handling Unit | Ventilation | 2F Common Public | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 9 | 12 | 30 | 7 | 7 I/O points carried, 12C cable; length 30 m (typical_range:boh_same_floor_field)
C0078 | PNL-AIR-2F | PAHU-2F (ME Contractor) | Precooled Air Handling Unit | Ventilation | 2F Common Public | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (typical_range:boh_same_floor_field)
C0079 | PNL-AIR-BSMT | PAHU-BSMT (BMS Contractor) | Precooled Air Handling Unit | Ventilation | Basement BOH | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 12 | 3 | 3 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0080 | PNL-AIR-BSMT | PAHU-BSMT (Equipment Supplier) | Precooled Air Handling Unit | Ventilation | Basement BOH | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 9 | 12 | 12 | 7 | 7 I/O points carried, 12C cable; length 12 m (typical_range:plant_room_same_room)
C0081 | PNL-AIR-BSMT | PAHU-BSMT (ME Contractor) | Precooled Air Handling Unit | Ventilation | Basement BOH | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0082 | PNL-AIR-ROOF | PAHU-ROOF (BMS Contractor) | Precooled Air Handling Unit | Ventilation | Roofdeck DOAS | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 12 | 3 | 3 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0083 | PNL-AIR-ROOF | PAHU-ROOF (Equipment Supplier) | Precooled Air Handling Unit | Ventilation | Roofdeck DOAS | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 9 | 12 | 12 | 7 | 7 I/O points carried, 12C cable; length 12 m (typical_range:plant_room_same_room)
C0084 | PNL-AIR-ROOF | PAHU-ROOF (ME Contractor) | Precooled Air Handling Unit | Ventilation | Roofdeck DOAS | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0085 | PNL-CH-PLANT-2F | CH-1 (Network) | Chiller (Package Water-Cooled) | Chilled Water Plant | 2F Chiller Plant Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0086 | PNL-CH-PLANT-2F | CH-2 (Network) | Chiller (Package Water-Cooled) | Chilled Water Plant | 2F Chiller Plant Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0087 | PNL-CH-PLANT-2F | BTU-CHW-MAIN (Network) | BTU Meter | Chilled Water Plant | 2F Chiller Plant Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0088 | PNL-PM-LG | PM-MAIN-LG (Network) | Multifunction Power Meter (Main) | Power Monitoring | Lower Ground Main Switchgear | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0089 | PNL-CH-PLANT-2F | PM-CHILLER (Network) | Multifunction Power Meter (Feeder) | Power Monitoring | 2F Chiller Plant Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0090 | PNL-CT-ROOF | PM-COOLING (Network) | Multifunction Power Meter (Feeder) | Power Monitoring | Roofdeck Cooling Tower | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0091 | PNL-AIR-2F | PM-AIR-2F (Network) | Multifunction Power Meter (Feeder) | Power Monitoring | 2F Common Public | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (typical_range:boh_same_floor_field)
C0092 | PNL-AIR-GF | PM-AIR-GF (Network) | Multifunction Power Meter (Feeder) | Power Monitoring | Ground Floor Lobby | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (typical_range:boh_same_floor_field)
C0093 | PNL-CASINO-GF | PM-CASINO (Network) | Multifunction Power Meter (Feeder) | Power Monitoring | Ground Floor Casino | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (typical_range:boh_same_floor_field)
C0094 | PNL-BLR-LG | PM-BOILER (Network) | Multifunction Power Meter (Feeder) | Power Monitoring | Lower Ground Boiler Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0095 | PNL-PL-LG | PM-PLUMB (Network) | Multifunction Power Meter (Feeder) | Power Monitoring | Lower Ground Calorifier Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0096 | PNL-PL-LG | PM-FIREPMP (Network) | Multifunction Power Meter (Feeder) | Power Monitoring | Lower Ground Boiler Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)

## Trunks
ID | From | To | Cable Type | Length (m) | Notes
T0097 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for 2nd Floor — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0098 | BMS Server Room (head-end) | All BMS panels at Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Basement — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0099 | BMS Server Room (head-end) | All BMS panels at Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Ground — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0100 | BMS Server Room (head-end) | All BMS panels at Lower Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Lower Ground — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0101 | BMS Server Room (head-end) | All BMS panels at Roofdeck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Roofdeck — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0102 | BMS Server Room (head-end) | All BMS panel controllers (MS/TP daisy-chain or branched) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 330 | MS/TP backbone interconnecting 11 BMS panels — refine after Q-008 layout review

## Panel Power Feeds
ID | From | To | Cable Type | Length (m) | Notes
P0103 | Local panelboard / EE-supplied feeder | PNL-AIR-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed_local)
P0104 | Local panelboard / EE-supplied feeder | PNL-AIR-3F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed_local)
P0105 | Local panelboard / EE-supplied feeder | PNL-AIR-BSMT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed_local)
P0106 | Local panelboard / EE-supplied feeder | PNL-AIR-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed_local)
P0107 | Local panelboard / EE-supplied feeder | PNL-AIR-ROOF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 35 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 35 m (typical_range:panel_power_feed_remote)
P0108 | Local panelboard / EE-supplied feeder | PNL-BLR-LG — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed_local)
P0109 | Local panelboard / EE-supplied feeder | PNL-CASINO-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed_local)
P0110 | Local panelboard / EE-supplied feeder | PNL-CH-PLANT-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed_local)
P0111 | Local panelboard / EE-supplied feeder | PNL-CT-ROOF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 35 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 35 m (typical_range:panel_power_feed_remote)
P0112 | Local panelboard / EE-supplied feeder | PNL-PL-LG — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed_local)
P0113 | Local panelboard / EE-supplied feeder | PNL-PM-LG — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed_local)