## Summary
A4 — Panel Schedule Summary
Total panels | 11
Total physical I/O | 383
Total HLI subpoints | 79
Total network drops | 12
Total I/O points | 474
Estimated total controllers | 20
Estimated total power (W) | 560

## Panel Schedule
Panel | Location | System Scope | Equipment Count | Physical I/O | HLI Subpoints | Network Drops | Total I/O | DDC Controllers | Network Gateway | Total Controllers | Power (W) | Enclosure
PNL-AIR-2F | 2F Common Public | Air Conditioning, Exhaust, Power Monitoring, Ventilation | 7 | 70 | 4 | 1 | 75 | 2 | 1 | 2 | 55 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-AIR-3F | 3F Amenity | Air Conditioning, Exhaust | 3 | 20 | 0 | 0 | 20 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-AIR-BSMT | Basement BOH | Exhaust, Ventilation | 3 | 18 | 0 | 0 | 18 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-AIR-GF | Ground Floor Lobby / Ground Floor Restaurant | Air Conditioning, Exhaust, Power Monitoring | 5 | 34 | 4 | 1 | 39 | 1 | 1 | 2 | 55 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-AIR-ROOF | Roofdeck DOAS | Exhaust, Hot Water, Ventilation | 7 | 70 | 0 | 0 | 70 | 2 | 0 | 2 | 50 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-BLR-LG | Lower Ground Boiler Room | Boiler, Power Monitoring | 3 | 32 | 4 | 1 | 37 | 1 | 1 | 2 | 55 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-CASINO-GF | Ground Floor Casino / Ground Floor Casino Lobby | Air Conditioning, Casino Air Conditioning, Power Monitoring | 5 | 45 | 4 | 1 | 50 | 2 | 1 | 2 | 55 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-CH-PLANT-2F | 2F Chiller Plant Room | Chilled Water Plant, Condenser Water Loop, Power Monitoring | 13 | 59 | 44 | 4 | 107 | 2 | 1 | 2 | 70 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-CT-ROOF | Roofdeck Cooling Tower | Condenser Water Loop, Power Monitoring | 5 | 22 | 4 | 1 | 27 | 1 | 1 | 2 | 55 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-PL-LG | Lower Ground Boiler Room / Lower Ground Calorifier Room | Hot Water, Power Monitoring | 7 | 13 | 8 | 2 | 23 | 1 | 1 | 2 | 60 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-PM-LG | Lower Ground Main Switchgear | Power Monitoring | 1 | 0 | 7 | 1 | 8 | 1 | 1 | 2 | 55 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare

## Equipment per Panel
Panel | Equipment Instance
PNL-AIR-2F | AHU-2F-A
PNL-AIR-2F | AHU-2F-B
PNL-AIR-2F | DOAS-2F
PNL-AIR-2F | EAS-GEN-2F
PNL-AIR-2F | EAS-TOILET-2F
PNL-AIR-2F | PAHU-2F
PNL-AIR-2F | PM-AIR-2F
PNL-AIR-3F | AHU-3F-AM
PNL-AIR-3F | EAS-GEN-3F
PNL-AIR-3F | EAS-TOILET-3F
PNL-AIR-BSMT | EAS-GEN-BSMT
PNL-AIR-BSMT | EAS-TOILET-BSMT
PNL-AIR-BSMT | PAHU-BSMT
PNL-AIR-GF | AHU-GF-LOB
PNL-AIR-GF | AHU-GF-REST
PNL-AIR-GF | EAS-GEN-GF
PNL-AIR-GF | EAS-TOILET-GF
PNL-AIR-GF | PM-AIR-GF
PNL-AIR-ROOF | CALOR-ROOF
PNL-AIR-ROOF | DOAS-RD1
PNL-AIR-ROOF | DOAS-RD2
PNL-AIR-ROOF | EAS-GEN-ROOF
PNL-AIR-ROOF | HP-ROOF-1
PNL-AIR-ROOF | HW-PUMP-ROOF-1
PNL-AIR-ROOF | PAHU-ROOF
PNL-BLR-LG | BLR-1
PNL-BLR-LG | BLR-2
PNL-BLR-LG | PM-BOILER
PNL-CASINO-GF | AHU-CASINO-1
PNL-CASINO-GF | AHU-CASINO-2
PNL-CASINO-GF | AHU-GF-CASINO
PNL-CASINO-GF | OZ-CASINO-1
PNL-CASINO-GF | PM-CASINO
PNL-CH-PLANT-2F | BTU-CHW-MAIN
PNL-CH-PLANT-2F | CH-1
PNL-CH-PLANT-2F | CH-2
PNL-CH-PLANT-2F | CHW-BYP
PNL-CH-PLANT-2F | CHW-RET-HDR
PNL-CH-PLANT-2F | CHW-SUP-HDR
PNL-CH-PLANT-2F | CHWP-1
PNL-CH-PLANT-2F | CHWP-2
PNL-CH-PLANT-2F | CHWP-3
PNL-CH-PLANT-2F | CWP-1
PNL-CH-PLANT-2F | CWP-2
PNL-CH-PLANT-2F | CWP-3
PNL-CH-PLANT-2F | PM-CHILLER
PNL-CT-ROOF | CT-1
PNL-CT-ROOF | CT-2
PNL-CT-ROOF | CT-COMMON
PNL-CT-ROOF | CW-HDR
PNL-CT-ROOF | PM-COOLING
PNL-PL-LG | CALOR-LG
PNL-PL-LG | HP-LG-1
PNL-PL-LG | HW-HEADERS-LG
PNL-PL-LG | HW-PUMP-LG-1
PNL-PL-LG | HW-PUMP-LG-2
PNL-PL-LG | PM-FIREPMP
PNL-PL-LG | PM-PLUMB
PNL-PM-LG | PM-MAIN-LG