## Summary
A3 — Cable Schedule, Audit View
Project | Kingsford Hotel Bacolod — BMS
Canonical source | A3-cable-schedule.yaml
How to record corrections | Edit the canonical YAML directly — add a verification: block to the affected row(s)
Totals
Total cables | 270
Total length (m) | 7,445
Field cables | 258
Trunk cables | 4
Panel power feeds | 8
Verification status
Status | Count | % of total
verified | 0 | 0%
needs_correction | 0 | 0%
uncertain | 0 | 0%
unverified | 270 | 100%
⚠ Known weak points
Cable lengths are estimates based on assumption A-001 (30 m average panel-to-device run, 80 m trunk per floor). Field-verified lengths typically vary by ±20% per cable. THIS IS THE SYSTEM'S WEAKEST AUTO-GENERATED QUANTITY — please verify before issuing the BOQ to the customer.
How corrections flow
1. Open A3-cable-schedule.yaml in any text editor.
2. Find the affected row by ID (column A in the Detail sheet).
3. Add a verification: block — see the 'Verification schema' sheet for the template.
4. Re-run: python3 _playbook/tools/generate-deliverables.py <project>
5. Corrections flow through B4 manhours, BOQ material costs, and final deliverables automatically.

## By Panel
Panel | Cable count | Total length (m)
PNL-2F | 71 | 2065
PNL-GF | 68 | 1960
PNL-3F | 65 | 1855
PNL-CHPLANT-GND | 27 | 324
PNL-RD | 15 | 270
PNL-BSMT | 7 | 227
PNL-BOH-2F | 4 | 128
PNL-HE-GF | 1 | 35
TOTAL (field cables) | 258 | 6864

## By Floor
Floor | Cable count | Total length (m)
2nd Floor | 73 | 2126
GF | 67 | 1925
3F | 64 | 1820
Plant Room | 26 | 312
Roofdeck | 14 | 252
panel | 8 | 237
Basement | 6 | 192
TOTAL | 258 | 6864

## By Cable Type
Cable type | Count | Total length (m)
4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 124 | 3245
4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 100 | 2830
4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 26 | 552
Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 8 | 237

## Detail (cables)
ID | From | To | Cable type | Length (m) | Status | Corrected (m) | Verified by | Date | Drawing ref | Notes
C0001 | PNL-3F | AHU-AMEN-3F (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 35 | unverified
C0002 | PNL-3F | AHU-AMEN-3F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 35 | unverified
C0003 | PNL-3F | AHU-AMEN-3F (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 35 | unverified
C0004 | PNL-2F | AHU-BALL-2F (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 35 | unverified
C0005 | PNL-2F | AHU-BALL-2F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 35 | unverified
C0006 | PNL-2F | AHU-BALL-2F (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 35 | unverified
C0007 | PNL-BOH-2F | AHU-BOH-2F (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 32 | unverified
C0008 | PNL-BOH-2F | AHU-BOH-2F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 32 | unverified
C0009 | PNL-BOH-2F | AHU-BOH-2F (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 32 | unverified
C0010 | PNL-BSMT | AHU-BOH-BSMT (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 32 | unverified
C0011 | PNL-BSMT | AHU-BOH-BSMT (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 32 | unverified
C0012 | PNL-BSMT | AHU-BOH-BSMT (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 32 | unverified
C0013 | PNL-GF | AHU-LOBBY-GF (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 35 | unverified
C0014 | PNL-GF | AHU-LOBBY-GF (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 35 | unverified
C0015 | PNL-GF | AHU-LOBBY-GF (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 35 | unverified
C0016 | PNL-2F | AHU-REST-2F (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 35 | unverified
C0017 | PNL-2F | AHU-REST-2F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 35 | unverified
C0018 | PNL-2F | AHU-REST-2F (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 35 | unverified
C0019 | PNL-CHPLANT-GND | CAL-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0020 | PNL-CHPLANT-GND | CAL-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0021 | PNL-CHPLANT-GND | CAL-3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0022 | PNL-CHPLANT-GND | CAL-4 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0023 | PNL-CHPLANT-GND | CAL-5 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0024 | PNL-CHPLANT-GND | CAL-6 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0025 | PNL-CHPLANT-GND | CHWP-1.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0026 | PNL-CHPLANT-GND | CHWP-1.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0027 | PNL-CHPLANT-GND | CHWP-1.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0028 | PNL-CHPLANT-GND | CHWP-1.STBY (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0029 | PNL-CHPLANT-GND | COWP-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0030 | PNL-CHPLANT-GND | COWP-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0031 | PNL-CHPLANT-GND | COWP-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0032 | PNL-RD | CT-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 18 | unverified
C0033 | PNL-RD | CT-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 18 | unverified
C0034 | PNL-RD | CT-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 18 | unverified
C0035 | PNL-RD | CT-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 18 | unverified
C0036 | PNL-RD | CT-3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 18 | unverified
C0037 | PNL-RD | CT-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 18 | unverified
C0038 | PNL-RD | CT-COMMON (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 18 | unverified
C0039 | PNL-2F | DOAS-2F (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 35 | unverified
C0040 | PNL-2F | DOAS-2F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 35 | unverified
C0041 | PNL-2F | DOAS-2F (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 35 | unverified
C0042 | PNL-GF | DOAS-GF (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 35 | unverified
C0043 | PNL-GF | DOAS-GF (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 35 | unverified
C0044 | PNL-GF | DOAS-GF (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 35 | unverified
C0045 | PNL-RD | DOAS-RD (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 18 | unverified
C0046 | PNL-RD | DOAS-RD (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 18 | unverified
C0047 | PNL-RD | DOAS-RD (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 18 | unverified
C0048 | PNL-2F | EAS-2F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 35 | unverified
C0049 | PNL-3F | EAS-3F (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 35 | unverified
C0050 | PNL-BSMT | EAS-BSMT (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 32 | unverified
C0051 | PNL-GF | EAS-GF (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 35 | unverified
C0052 | PNL-2F | FCU-2F.01 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0053 | PNL-2F | FCU-2F.01 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0054 | PNL-2F | FCU-2F.02 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0055 | PNL-2F | FCU-2F.02 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0056 | PNL-2F | FCU-2F.03 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0057 | PNL-2F | FCU-2F.03 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0058 | PNL-2F | FCU-2F.04 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0059 | PNL-2F | FCU-2F.04 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0060 | PNL-2F | FCU-2F.05 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0061 | PNL-2F | FCU-2F.05 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0062 | PNL-2F | FCU-2F.06 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0063 | PNL-2F | FCU-2F.06 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0064 | PNL-2F | FCU-2F.07 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0065 | PNL-2F | FCU-2F.07 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0066 | PNL-2F | FCU-2F.08 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0067 | PNL-2F | FCU-2F.08 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0068 | PNL-2F | FCU-2F.09 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0069 | PNL-2F | FCU-2F.09 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0070 | PNL-2F | FCU-2F.10 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0071 | PNL-2F | FCU-2F.10 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0072 | PNL-2F | FCU-2F.11 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0073 | PNL-2F | FCU-2F.11 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0074 | PNL-2F | FCU-2F.12 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0075 | PNL-2F | FCU-2F.12 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0076 | PNL-2F | FCU-2F.13 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0077 | PNL-2F | FCU-2F.13 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0078 | PNL-2F | FCU-2F.14 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0079 | PNL-2F | FCU-2F.14 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0080 | PNL-2F | FCU-2F.15 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0081 | PNL-2F | FCU-2F.15 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0082 | PNL-2F | FCU-2F.16 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0083 | PNL-2F | FCU-2F.16 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0084 | PNL-2F | FCU-2F.17 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0085 | PNL-2F | FCU-2F.17 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0086 | PNL-2F | FCU-2F.18 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0087 | PNL-2F | FCU-2F.18 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0088 | PNL-2F | FCU-2F.19 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0089 | PNL-2F | FCU-2F.19 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0090 | PNL-2F | FCU-2F.20 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0091 | PNL-2F | FCU-2F.20 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0092 | PNL-2F | FCU-2F.21 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0093 | PNL-2F | FCU-2F.21 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0094 | PNL-2F | FCU-2F.22 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0095 | PNL-2F | FCU-2F.22 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0096 | PNL-2F | FCU-2F.23 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0097 | PNL-2F | FCU-2F.23 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0098 | PNL-2F | FCU-2F.24 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0099 | PNL-2F | FCU-2F.24 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0100 | PNL-2F | FCU-2F.25 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0101 | PNL-2F | FCU-2F.25 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0102 | PNL-2F | FCU-2F.26 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0103 | PNL-2F | FCU-2F.26 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0104 | PNL-2F | FCU-2F.27 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0105 | PNL-2F | FCU-2F.27 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0106 | PNL-2F | FCU-2F.28 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0107 | PNL-2F | FCU-2F.28 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0108 | PNL-2F | FCU-2F.29 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0109 | PNL-2F | FCU-2F.29 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0110 | PNL-2F | FCU-2F.30 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0111 | PNL-2F | FCU-2F.30 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0112 | PNL-3F | FCU-3F.01 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0113 | PNL-3F | FCU-3F.01 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0114 | PNL-3F | FCU-3F.02 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0115 | PNL-3F | FCU-3F.02 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0116 | PNL-3F | FCU-3F.03 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0117 | PNL-3F | FCU-3F.03 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0118 | PNL-3F | FCU-3F.04 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0119 | PNL-3F | FCU-3F.04 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0120 | PNL-3F | FCU-3F.05 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0121 | PNL-3F | FCU-3F.05 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0122 | PNL-3F | FCU-3F.06 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0123 | PNL-3F | FCU-3F.06 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0124 | PNL-3F | FCU-3F.07 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0125 | PNL-3F | FCU-3F.07 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0126 | PNL-3F | FCU-3F.08 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0127 | PNL-3F | FCU-3F.08 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0128 | PNL-3F | FCU-3F.09 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0129 | PNL-3F | FCU-3F.09 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0130 | PNL-3F | FCU-3F.10 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0131 | PNL-3F | FCU-3F.10 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0132 | PNL-3F | FCU-3F.11 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0133 | PNL-3F | FCU-3F.11 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0134 | PNL-3F | FCU-3F.12 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0135 | PNL-3F | FCU-3F.12 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0136 | PNL-3F | FCU-3F.13 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0137 | PNL-3F | FCU-3F.13 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0138 | PNL-3F | FCU-3F.14 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0139 | PNL-3F | FCU-3F.14 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0140 | PNL-3F | FCU-3F.15 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0141 | PNL-3F | FCU-3F.15 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0142 | PNL-3F | FCU-3F.16 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0143 | PNL-3F | FCU-3F.16 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0144 | PNL-3F | FCU-3F.17 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0145 | PNL-3F | FCU-3F.17 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0146 | PNL-3F | FCU-3F.18 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0147 | PNL-3F | FCU-3F.18 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0148 | PNL-3F | FCU-3F.19 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0149 | PNL-3F | FCU-3F.19 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0150 | PNL-3F | FCU-3F.20 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0151 | PNL-3F | FCU-3F.20 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0152 | PNL-3F | FCU-3F.21 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0153 | PNL-3F | FCU-3F.21 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0154 | PNL-3F | FCU-3F.22 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0155 | PNL-3F | FCU-3F.22 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0156 | PNL-3F | FCU-3F.23 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0157 | PNL-3F | FCU-3F.23 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0158 | PNL-3F | FCU-3F.24 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0159 | PNL-3F | FCU-3F.24 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0160 | PNL-3F | FCU-3F.25 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0161 | PNL-3F | FCU-3F.25 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0162 | PNL-3F | FCU-3F.26 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0163 | PNL-3F | FCU-3F.26 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0164 | PNL-3F | FCU-3F.27 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0165 | PNL-3F | FCU-3F.27 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0166 | PNL-3F | FCU-3F.28 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0167 | PNL-3F | FCU-3F.28 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0168 | PNL-3F | FCU-3F.29 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0169 | PNL-3F | FCU-3F.29 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0170 | PNL-3F | FCU-3F.30 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0171 | PNL-3F | FCU-3F.30 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0172 | PNL-GF | FCU-GF.01 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0173 | PNL-GF | FCU-GF.01 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0174 | PNL-GF | FCU-GF.02 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0175 | PNL-GF | FCU-GF.02 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0176 | PNL-GF | FCU-GF.03 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0177 | PNL-GF | FCU-GF.03 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0178 | PNL-GF | FCU-GF.04 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0179 | PNL-GF | FCU-GF.04 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0180 | PNL-GF | FCU-GF.05 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0181 | PNL-GF | FCU-GF.05 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0182 | PNL-GF | FCU-GF.06 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0183 | PNL-GF | FCU-GF.06 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0184 | PNL-GF | FCU-GF.07 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0185 | PNL-GF | FCU-GF.07 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0186 | PNL-GF | FCU-GF.08 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0187 | PNL-GF | FCU-GF.08 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0188 | PNL-GF | FCU-GF.09 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0189 | PNL-GF | FCU-GF.09 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0190 | PNL-GF | FCU-GF.10 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0191 | PNL-GF | FCU-GF.10 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0192 | PNL-GF | FCU-GF.11 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0193 | PNL-GF | FCU-GF.11 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0194 | PNL-GF | FCU-GF.12 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0195 | PNL-GF | FCU-GF.12 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0196 | PNL-GF | FCU-GF.13 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0197 | PNL-GF | FCU-GF.13 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0198 | PNL-GF | FCU-GF.14 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0199 | PNL-GF | FCU-GF.14 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0200 | PNL-GF | FCU-GF.15 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0201 | PNL-GF | FCU-GF.15 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0202 | PNL-GF | FCU-GF.16 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0203 | PNL-GF | FCU-GF.16 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0204 | PNL-GF | FCU-GF.17 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0205 | PNL-GF | FCU-GF.17 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0206 | PNL-GF | FCU-GF.18 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0207 | PNL-GF | FCU-GF.18 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0208 | PNL-GF | FCU-GF.19 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0209 | PNL-GF | FCU-GF.19 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0210 | PNL-GF | FCU-GF.20 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0211 | PNL-GF | FCU-GF.20 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0212 | PNL-GF | FCU-GF.21 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0213 | PNL-GF | FCU-GF.21 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0214 | PNL-GF | FCU-GF.22 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0215 | PNL-GF | FCU-GF.22 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0216 | PNL-GF | FCU-GF.23 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0217 | PNL-GF | FCU-GF.23 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0218 | PNL-GF | FCU-GF.24 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0219 | PNL-GF | FCU-GF.24 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0220 | PNL-GF | FCU-GF.25 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0221 | PNL-GF | FCU-GF.25 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0222 | PNL-GF | FCU-GF.26 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0223 | PNL-GF | FCU-GF.26 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0224 | PNL-GF | FCU-GF.27 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0225 | PNL-GF | FCU-GF.27 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0226 | PNL-GF | FCU-GF.28 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0227 | PNL-GF | FCU-GF.28 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0228 | PNL-GF | FCU-GF.29 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0229 | PNL-GF | FCU-GF.29 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0230 | PNL-GF | FCU-GF.30 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 28 | unverified
C0231 | PNL-GF | FCU-GF.30 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0232 | PNL-CHPLANT-GND | HDR-CHW-BP (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0233 | PNL-CHPLANT-GND | HDR-CHWR (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0234 | PNL-CHPLANT-GND | HDR-CHWS (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0235 | PNL-RD | HDR-COW (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 18 | unverified
C0236 | PNL-CHPLANT-GND | HDR-HW (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 12 | unverified
C0237 | PNL-CHPLANT-GND | HP-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0238 | PNL-CHPLANT-GND | HP-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0239 | PNL-CHPLANT-GND | HP-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0240 | PNL-RD | PAHU-RD (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 18 | unverified
C0241 | PNL-RD | PAHU-RD (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 18 | unverified
C0242 | PNL-RD | PAHU-RD (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 18 | unverified
C0243 | PNL-CHPLANT-GND | RP-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0244 | PNL-CHPLANT-GND | RP-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0245 | PNL-CHPLANT-GND | RP-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0246 | PNL-CHPLANT-GND | RP-4 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0247 | PNL-CHPLANT-GND | RP-5 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0248 | PNL-CHPLANT-GND | RP-6 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | unverified
C0249 | PNL-BSMT | SB-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 32 | unverified
C0250 | PNL-BSMT | SB-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 32 | unverified
C0251 | PNL-RD | NET-PNL-RD (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 18 | unverified
C0252 | PNL-3F | NET-PNL-3F (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 35 | unverified
C0253 | PNL-2F | NET-PNL-2F (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 35 | unverified
C0254 | PNL-GF | NET-PNL-GF (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 35 | unverified
C0255 | PNL-BSMT | NET-PNL-BSMT (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 35 | unverified
C0256 | PNL-CHPLANT-GND | NET-PNL-CHPLANT-GND (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0257 | PNL-BOH-2F | NET-PNL-BOH-2F (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 32 | unverified
C0258 | PNL-HE-GF | NET-PNL-HE-GF (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 35 | unverified
T0259 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0260 | BMS Server Room (head-end) | All BMS panels at Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0261 | BMS Server Room (head-end) | All BMS panels at Roofdeck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0262 | BMS Server Room (head-end) | BMS panel controllers (per topology id mstp_main_backbone) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 245 | unverified
P0263 | Local panelboard / EE-supplied feeder | PNL-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | unverified
P0264 | Local panelboard / EE-supplied feeder | PNL-3F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | unverified
P0265 | Local panelboard / EE-supplied feeder | PNL-BOH-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | unverified
P0266 | Local panelboard / EE-supplied feeder | PNL-BSMT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | unverified
P0267 | Local panelboard / EE-supplied feeder | PNL-CHPLANT-GND — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | unverified
P0268 | Local panelboard / EE-supplied feeder | PNL-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | unverified
P0269 | Local panelboard / EE-supplied feeder | PNL-HE-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | unverified
P0270 | Local panelboard / EE-supplied feeder | PNL-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | unverified

## Verification schema
How to record verification / corrections in A3-cable-schedule.yaml
Find the affected row in the YAML by ID (Detail sheet column A) and add a verification: block:
- id: C0001
from: PNL-CH-PLANT-GND
to: CH-1 (BMS Contractor)
cable_type: 4C × 1.5 mm² shielded FRLS
length_m: 30
verification: # ADDED by team
status: needs_correction # unverified ¦ verified ¦ needs_correction ¦ uncertain
corrected_length_m: 42 # team's measured / confirmed value
verified_by: J. Cruz
verified_date: 2026-05-10
drawing_ref: "EE-09 grid B-2"
notes: ""
After saving, re-run: python3 _playbook/tools/generate-deliverables.py <project>
Corrections propagate to B4 manhours, BOQ, and final deliverables automatically.
Recommended verification methods (priority order):
1. Site walkthrough with measurement (most accurate; for cable lengths, after structural completion).
2. Properly-scaled architectural drawings.
3. Mechanical contractor's tray layout combined with BMS panel locations.
4. A-001 default with ±20% contingency in BOQ — last resort.