## Summary
A4 — Panel Schedule, Audit View
Project | Kingsford Hotel Bacolod — BMS
Canonical source | A4-panel-schedule.yaml
How to record corrections | Edit the canonical YAML directly — add a verification: block to the affected row(s)
Totals
Total panels | 8
Total physical I/O | 523
Total HLI sub-points | 23
Total controllers | 21
Verification status
Status | Count | % of total
verified | 0 | 0%
needs_correction | 0 | 0%
uncertain | 0 | 0%
unverified | 8 | 100%
⚠ Known weak points
Verify panel locations against architectural drawings. Confirm proximity to served equipment, panel-room space allocation, and access for maintenance.
How corrections flow
Edit A4-panel-schedule.yaml — add a verification: block to the panel row when location is confirmed or revised.

## Detail
Panel | Location | Equipment served | Phys I/O | HLI | Network drops | Controllers | Power (W) | Status | Verified by | Drawing ref | Notes
PNL-2F | 2F / panel | 35 | 138 | 0 | 1 | 4 | 105 | unverified
PNL-3F | 3F / panel | 33 | 105 | 0 | 1 | 3 | 80 | unverified
PNL-BOH-2F | 2F / panel | 2 | 12 | 0 | 1 | 2 | 55 | unverified
PNL-BSMT | Basement / panel | 4 | 23 | 0 | 1 | 2 | 55 | unverified
PNL-CHPLANT-GND | Plant Room / Plant Room (Basement) / panel | 31 | 65 | 10 | 1 | 2 | 55 | unverified
PNL-GF | GF / Main Switchgear / Sub-Distribution Board / panel | 47 | 126 | 13 | 1 | 4 | 105 | unverified
PNL-HE-GF | panel | 1 | 0 | 0 | 1 | 2 | 55 | unverified
PNL-RD | Roofdeck / panel | 8 | 54 | 0 | 1 | 2 | 55 | unverified

## Verification schema
How to record verification / corrections in A4-panel-schedule.yaml
Find the affected row in the YAML by ID (Detail sheet column A) and add a verification: block:
- id: PNL-AHU-3F
verification: # ADDED by team
status: needs_correction # unverified ¦ verified ¦ needs_correction ¦ uncertain
corrected_location: 3F Mech Room A # team's measured / confirmed value
verified_by: J. Cruz
verified_date: 2026-05-10
drawing_ref: "EE-09 grid B-2"
notes: ""
After saving, re-run: python3 _playbook/tools/generate-deliverables.py <project>
Corrections propagate to B4 manhours, BOQ, and final deliverables automatically.
Recommended verification methods (priority order):
1. Site walkthrough with measurement (most accurate; for cable lengths, after structural completion).
2. Properly-scaled architectural drawings.
3. Mechanical contractor's tray layout combined with BMS panel locations.
4. A-001 default with ±20% contingency in BOQ — last resort.