## Summary
A1 — Consolidated I/O List Summary
Project | Kingsford Hotel Bacolod — BMS
Total I/O rows | 554
By type
DI | 203
DO | 183
AI | 93
AO | 44
HLI | 23
Network | 8
By C/O
Equipment Supplier | 328
ME Contractor | 128
BMS Contractor | 98
By system
VENT-FCU | 270
VENT-AHU | 72
VENT-DOAS | 63
HVAC-Pumps | 29
HVAC-Cooling-Towers | 20
HVAC-Chillers | 16
Power-EE | 13
VENT-EAS | 12
PL-RecircPumps | 12
VENT-PAHU | 10
PL-HeatPumps | 9
PL-Boiler | 8
Network | 8
PL-Calorifiers | 6
PL-HotWater | 6
By panel
PNL-GF | 140
PNL-2F | 139
PNL-3F | 106
PNL-CHPLANT-GND | 76
PNL-RD | 55
PNL-BSMT | 24
PNL-BOH-2F | 13
PNL-HE-GF | 1

## All IO Points
ID | System | Equipment Class | Equipment Instance | Location | Point Description | Type | Field Device | C/O | DoO Ref | Panel | Source | Notes
P0001 | HVAC-Chillers | Chiller (Package Water-Cooled) | CH-1 | Plant Room (Basement) | Chiller 1 BACnet HLI (status, motor current, kW, evap/cond temps, refrigerant pressures, oil sump T+P) | HLI | BACnet IP card | Equipment Supplier | DoO: Chiller plant sequencing | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0002 | HVAC-Chillers | CHW Supply Main Header | HDR-CHWS | Plant Room | Entering Chilled Water Temperature CH-1 | AI | Temperature Sensor | BMS Contractor | DoO: Chiller | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0003 | HVAC-Chillers | CHW Return Main Header | HDR-CHWR | Plant Room | Leaving Chilled Water Temperature CH-1 | AI | Temperature Sensor | BMS Contractor | DoO: Chiller | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0004 | HVAC-Chillers | Condenser Water Header | HDR-COW | Roofdeck | Condenser Water Supply T CH-1 | AI | Temperature Sensor | BMS Contractor | DoO: Chiller | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0005 | HVAC-Chillers | Chiller (Package Water-Cooled) | CH-2 | Plant Room (Basement) | Chiller 2 BACnet HLI (status, motor current, kW, evap/cond temps, refrigerant pressures, oil sump T+P) | HLI | BACnet IP card | Equipment Supplier | DoO: Chiller plant sequencing | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0006 | HVAC-Chillers | CHW Supply Main Header | HDR-CHWS | Plant Room | Entering Chilled Water Temperature CH-2 | AI | Temperature Sensor | BMS Contractor | DoO: Chiller | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0007 | HVAC-Chillers | CHW Return Main Header | HDR-CHWR | Plant Room | Leaving Chilled Water Temperature CH-2 | AI | Temperature Sensor | BMS Contractor | DoO: Chiller | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0008 | HVAC-Chillers | Condenser Water Header | HDR-COW | Roofdeck | Condenser Water Supply T CH-2 | AI | Temperature Sensor | BMS Contractor | DoO: Chiller | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0009 | HVAC-Chillers | Chiller (Package Water-Cooled) | CH-3 | Plant Room (Basement) | Chiller 3 BACnet HLI (status, motor current, kW, evap/cond temps, refrigerant pressures, oil sump T+P) | HLI | BACnet IP card | Equipment Supplier | DoO: Chiller plant sequencing | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0010 | HVAC-Chillers | CHW Supply Main Header | HDR-CHWS | Plant Room | Entering Chilled Water Temperature CH-3 | AI | Temperature Sensor | BMS Contractor | DoO: Chiller | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0011 | HVAC-Chillers | CHW Return Main Header | HDR-CHWR | Plant Room | Leaving Chilled Water Temperature CH-3 | AI | Temperature Sensor | BMS Contractor | DoO: Chiller | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0012 | HVAC-Chillers | Condenser Water Header | HDR-COW | Roofdeck | Condenser Water Supply T CH-3 | AI | Temperature Sensor | BMS Contractor | DoO: Chiller | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0013 | HVAC-Chillers | CHW Bypass Header | HDR-CHW-BP | Plant Room | CHW differential pressure | AI | Differential Pressure Sensor | BMS Contractor | DoO: Plant | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0014 | HVAC-Chillers | CHW Bypass Header | HDR-CHW-BP | Plant Room | Bypass valve command | AO | Electric Valve Actuator | BMS Contractor | DoO: Plant | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0015 | HVAC-Chillers | CHW Bypass Header | HDR-CHW-BP | Plant Room | Bypass valve status | AI | Position Feedback | BMS Contractor | DoO: Plant | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0016 | HVAC-Chillers | BTU Meter | BTU-CHWS-MAIN | Plant Room | Plant CHW BTU (Modbus: flow, supply T, return T, kW, kWh) | HLI | Ultrasonic BTU Meter | BMS Contractor | DoO: Energy reporting | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus
P0017 | HVAC-Pumps | Primary CHW Pump | CHWP-1.1 | Plant Room | Pump motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0018 | HVAC-Pumps | Primary CHW Pump | CHWP-1.1 | Plant Room | Pump HOA status | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0019 | HVAC-Pumps | Primary CHW Pump | CHWP-1.1 | Plant Room | Pump trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0020 | HVAC-Pumps | Primary CHW Pump | CHWP-1.1 | Plant Room | VFD speed feedback (BACnet HLI) | HLI | VFD BACnet card | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0021 | HVAC-Pumps | Primary CHW Pump | CHWP-1.1 | Plant Room | VFD speed command (BACnet HLI) | HLI | VFD BACnet card | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0022 | HVAC-Pumps | Primary CHW Pump | CHWP-1.2 | Plant Room | Pump motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0023 | HVAC-Pumps | Primary CHW Pump | CHWP-1.2 | Plant Room | Pump HOA status | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0024 | HVAC-Pumps | Primary CHW Pump | CHWP-1.2 | Plant Room | Pump trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0025 | HVAC-Pumps | Primary CHW Pump | CHWP-1.2 | Plant Room | VFD speed feedback (BACnet HLI) | HLI | VFD BACnet card | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0026 | HVAC-Pumps | Primary CHW Pump | CHWP-1.2 | Plant Room | VFD speed command (BACnet HLI) | HLI | VFD BACnet card | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0027 | HVAC-Pumps | Primary CHW Pump | CHWP-1.3 | Plant Room | Pump motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0028 | HVAC-Pumps | Primary CHW Pump | CHWP-1.3 | Plant Room | Pump HOA status | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0029 | HVAC-Pumps | Primary CHW Pump | CHWP-1.3 | Plant Room | Pump trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0030 | HVAC-Pumps | Primary CHW Pump | CHWP-1.3 | Plant Room | VFD speed feedback (BACnet HLI) | HLI | VFD BACnet card | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0031 | HVAC-Pumps | Primary CHW Pump | CHWP-1.3 | Plant Room | VFD speed command (BACnet HLI) | HLI | VFD BACnet card | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0032 | HVAC-Pumps | Primary CHW Pump (Standby) | CHWP-1.STBY | Plant Room | Pump motor status (standby) | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0033 | HVAC-Pumps | Primary CHW Pump (Standby) | CHWP-1.STBY | Plant Room | Pump trip alarm (standby) | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0034 | HVAC-Pumps | Condenser Water Pump | COWP-1 | Plant Room | Pump motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0035 | HVAC-Pumps | Condenser Water Pump | COWP-1 | Plant Room | Pump HOA status | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0036 | HVAC-Pumps | Condenser Water Pump | COWP-1 | Plant Room | Pump trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0037 | HVAC-Pumps | Condenser Water Pump | COWP-1 | Plant Room | Pump start command | DO | Relay Output | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0038 | HVAC-Pumps | Condenser Water Pump | COWP-2 | Plant Room | Pump motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0039 | HVAC-Pumps | Condenser Water Pump | COWP-2 | Plant Room | Pump HOA status | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0040 | HVAC-Pumps | Condenser Water Pump | COWP-2 | Plant Room | Pump trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0041 | HVAC-Pumps | Condenser Water Pump | COWP-2 | Plant Room | Pump start command | DO | Relay Output | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0042 | HVAC-Pumps | Condenser Water Pump | COWP-3 | Plant Room | Pump motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0043 | HVAC-Pumps | Condenser Water Pump | COWP-3 | Plant Room | Pump HOA status | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0044 | HVAC-Pumps | Condenser Water Pump | COWP-3 | Plant Room | Pump trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0045 | HVAC-Pumps | Condenser Water Pump | COWP-3 | Plant Room | Pump start command | DO | Relay Output | Equipment Supplier | DoO: Pumps | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0046 | HVAC-Cooling-Towers | Cooling Tower | CT-1 | Roofdeck | Fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0047 | HVAC-Cooling-Towers | Cooling Tower | CT-1 | Roofdeck | Fan HOA status | DI | Auxiliary Contact | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0048 | HVAC-Cooling-Towers | Cooling Tower | CT-1 | Roofdeck | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0049 | HVAC-Cooling-Towers | Cooling Tower | CT-1 | Roofdeck | Fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0050 | HVAC-Cooling-Towers | Cooling Tower | CT-1 | Roofdeck | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0051 | HVAC-Cooling-Towers | Cooling Tower | CT-1 | Roofdeck | Basin water level low | DI | Float Switch | BMS Contractor | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0052 | HVAC-Cooling-Towers | Cooling Tower | CT-2 | Roofdeck | Fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0053 | HVAC-Cooling-Towers | Cooling Tower | CT-2 | Roofdeck | Fan HOA status | DI | Auxiliary Contact | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0054 | HVAC-Cooling-Towers | Cooling Tower | CT-2 | Roofdeck | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0055 | HVAC-Cooling-Towers | Cooling Tower | CT-2 | Roofdeck | Fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0056 | HVAC-Cooling-Towers | Cooling Tower | CT-2 | Roofdeck | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0057 | HVAC-Cooling-Towers | Cooling Tower | CT-2 | Roofdeck | Basin water level low | DI | Float Switch | BMS Contractor | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0058 | HVAC-Cooling-Towers | Cooling Tower | CT-3 | Roofdeck | Fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0059 | HVAC-Cooling-Towers | Cooling Tower | CT-3 | Roofdeck | Fan HOA status | DI | Auxiliary Contact | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0060 | HVAC-Cooling-Towers | Cooling Tower | CT-3 | Roofdeck | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0061 | HVAC-Cooling-Towers | Cooling Tower | CT-3 | Roofdeck | Fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0062 | HVAC-Cooling-Towers | Cooling Tower | CT-3 | Roofdeck | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0063 | HVAC-Cooling-Towers | Cooling Tower | CT-3 | Roofdeck | Basin water level low | DI | Float Switch | BMS Contractor | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0064 | HVAC-Cooling-Towers | Cooling Tower (Common) | CT-COMMON | Roofdeck | Outdoor air temperature | AI | Outdoor Temperature Sensor | BMS Contractor | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0065 | HVAC-Cooling-Towers | Cooling Tower (Common) | CT-COMMON | Roofdeck | Outdoor air relative humidity | AI | Humidity Sensor | BMS Contractor | DoO: Cooling tower | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0066 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | OA Temperature | AI | Temperature Sensor | BMS Contractor | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0067 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | OA Humidity | AI | Humidity Sensor | BMS Contractor | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0068 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | OA Flow | AI | Flow Sensor | BMS Contractor | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0069 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Indoor Mixed Air T | AI | Temperature Sensor | Equipment Supplier | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0070 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Indoor Mixed Air RH | AI | Humidity Sensor | Equipment Supplier | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0071 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Indoor Supply Air T | AI | Temperature Sensor | BMS Contractor | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0072 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Indoor Exhaust Air T | AI | Temperature Sensor | BMS Contractor | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0073 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Recovery wheel motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0074 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Recovery wheel trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0075 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Supply fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0076 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Supply fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0077 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Supply fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0078 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Supply fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0079 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Exhaust fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0080 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Exhaust fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0081 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Exhaust fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0082 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | Exhaust fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0083 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | OA motorized damper status | DI | Damper Position Switch | ME Contractor | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0084 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | OA motorized damper command | AO | Damper Actuator | ME Contractor | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0085 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | CHWS coil valve status | DI | Position Feedback | ME Contractor | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0086 | VENT-DOAS | DOAS Unit | DOAS-RD | Roofdeck | CHWS coil valve command | AO | Electric Valve Actuator | ME Contractor | DoO: DOAS | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0087 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | OA Temperature | AI | Temperature Sensor | BMS Contractor | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0088 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | OA Humidity | AI | Humidity Sensor | BMS Contractor | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0089 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | OA Flow | AI | Flow Sensor | BMS Contractor | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0090 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Indoor Mixed Air T | AI | Temperature Sensor | Equipment Supplier | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0091 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Indoor Mixed Air RH | AI | Humidity Sensor | Equipment Supplier | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0092 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Indoor Supply Air T | AI | Temperature Sensor | BMS Contractor | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0093 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Indoor Exhaust Air T | AI | Temperature Sensor | BMS Contractor | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0094 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Recovery wheel motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0095 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Recovery wheel trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0096 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Supply fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0097 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Supply fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0098 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Supply fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0099 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Supply fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0100 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Exhaust fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0101 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Exhaust fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0102 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Exhaust fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0103 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | Exhaust fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0104 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | OA motorized damper status | DI | Damper Position Switch | ME Contractor | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0105 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | OA motorized damper command | AO | Damper Actuator | ME Contractor | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0106 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | CHWS coil valve status | DI | Position Feedback | ME Contractor | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0107 | VENT-DOAS | DOAS Unit | DOAS-GF | GF | CHWS coil valve command | AO | Electric Valve Actuator | ME Contractor | DoO: DOAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0108 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | OA Temperature | AI | Temperature Sensor | BMS Contractor | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0109 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | OA Humidity | AI | Humidity Sensor | BMS Contractor | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0110 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | OA Flow | AI | Flow Sensor | BMS Contractor | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0111 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Indoor Mixed Air T | AI | Temperature Sensor | Equipment Supplier | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0112 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Indoor Mixed Air RH | AI | Humidity Sensor | Equipment Supplier | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0113 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Indoor Supply Air T | AI | Temperature Sensor | BMS Contractor | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0114 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Indoor Exhaust Air T | AI | Temperature Sensor | BMS Contractor | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0115 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Recovery wheel motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0116 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Recovery wheel trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0117 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Supply fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0118 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Supply fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0119 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Supply fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0120 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Supply fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0121 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Exhaust fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0122 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Exhaust fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0123 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Exhaust fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0124 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | Exhaust fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0125 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | OA motorized damper status | DI | Damper Position Switch | ME Contractor | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0126 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | OA motorized damper command | AO | Damper Actuator | ME Contractor | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0127 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | CHWS coil valve status | DI | Position Feedback | ME Contractor | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0128 | VENT-DOAS | DOAS Unit | DOAS-2F | 2F | CHWS coil valve command | AO | Electric Valve Actuator | ME Contractor | DoO: DOAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0129 | VENT-PAHU | Precooled Air Handling Unit | PAHU-RD | Roofdeck | OA temperature | AI | Temperature Sensor | BMS Contractor | DoO: PAHU | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0130 | VENT-PAHU | Precooled Air Handling Unit | PAHU-RD | Roofdeck | OA flow | AI | Flow Sensor | BMS Contractor | DoO: PAHU | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0131 | VENT-PAHU | Precooled Air Handling Unit | PAHU-RD | Roofdeck | Supply T | AI | Temperature Sensor | BMS Contractor | DoO: PAHU | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0132 | VENT-PAHU | Precooled Air Handling Unit | PAHU-RD | Roofdeck | Fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: PAHU | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0133 | VENT-PAHU | Precooled Air Handling Unit | PAHU-RD | Roofdeck | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: PAHU | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0134 | VENT-PAHU | Precooled Air Handling Unit | PAHU-RD | Roofdeck | Fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: PAHU | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0135 | VENT-PAHU | Precooled Air Handling Unit | PAHU-RD | Roofdeck | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: PAHU | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0136 | VENT-PAHU | Precooled Air Handling Unit | PAHU-RD | Roofdeck | OA damper command | AO | Damper Actuator | Equipment Supplier | DoO: PAHU | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0137 | VENT-PAHU | Precooled Air Handling Unit | PAHU-RD | Roofdeck | CHWS valve command | AO | Electric Valve Actuator | ME Contractor | DoO: PAHU | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0138 | VENT-PAHU | Precooled Air Handling Unit | PAHU-RD | Roofdeck | CHWS valve status | DI | Position Feedback | ME Contractor | DoO: PAHU | PNL-RD | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0139 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-LOBBY-GF | GF | Return Air T | AI | Temperature Sensor | BMS Contractor | DoO: AHU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0140 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-LOBBY-GF | GF | Return Air RH | AI | Humidity Sensor | BMS Contractor | DoO: AHU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0141 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-LOBBY-GF | GF | Supply Air T | AI | Temperature Sensor | BMS Contractor | DoO: AHU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0142 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-LOBBY-GF | GF | Return CO2 | AI | CO2 Sensor | BMS Contractor | DoO: AHU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0143 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-LOBBY-GF | GF | Fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: AHU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0144 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-LOBBY-GF | GF | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: AHU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0145 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-LOBBY-GF | GF | Fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: AHU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0146 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-LOBBY-GF | GF | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: AHU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0147 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-LOBBY-GF | GF | CHWS valve command | AO | Electric Valve Actuator | ME Contractor | DoO: AHU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0148 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-LOBBY-GF | GF | CHWS valve status | DI | Position Feedback | ME Contractor | DoO: AHU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0149 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-LOBBY-GF | GF | OA damper command | AO | Damper Actuator | ME Contractor | DoO: AHU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0150 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-LOBBY-GF | GF | RA damper command | AO | Damper Actuator | ME Contractor | DoO: AHU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0151 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BALL-2F | 2F | Return Air T | AI | Temperature Sensor | BMS Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0152 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BALL-2F | 2F | Return Air RH | AI | Humidity Sensor | BMS Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0153 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BALL-2F | 2F | Supply Air T | AI | Temperature Sensor | BMS Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0154 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BALL-2F | 2F | Return CO2 | AI | CO2 Sensor | BMS Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0155 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BALL-2F | 2F | Fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0156 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BALL-2F | 2F | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0157 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BALL-2F | 2F | Fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0158 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BALL-2F | 2F | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0159 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BALL-2F | 2F | CHWS valve command | AO | Electric Valve Actuator | ME Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0160 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BALL-2F | 2F | CHWS valve status | DI | Position Feedback | ME Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0161 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BALL-2F | 2F | OA damper command | AO | Damper Actuator | ME Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0162 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BALL-2F | 2F | RA damper command | AO | Damper Actuator | ME Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0163 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-REST-2F | 2F | Return Air T | AI | Temperature Sensor | BMS Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0164 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-REST-2F | 2F | Return Air RH | AI | Humidity Sensor | BMS Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0165 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-REST-2F | 2F | Supply Air T | AI | Temperature Sensor | BMS Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0166 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-REST-2F | 2F | Return CO2 | AI | CO2 Sensor | BMS Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0167 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-REST-2F | 2F | Fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0168 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-REST-2F | 2F | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0169 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-REST-2F | 2F | Fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0170 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-REST-2F | 2F | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0171 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-REST-2F | 2F | CHWS valve command | AO | Electric Valve Actuator | ME Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0172 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-REST-2F | 2F | CHWS valve status | DI | Position Feedback | ME Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0173 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-REST-2F | 2F | OA damper command | AO | Damper Actuator | ME Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0174 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-REST-2F | 2F | RA damper command | AO | Damper Actuator | ME Contractor | DoO: AHU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0175 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-AMEN-3F | 3F | Return Air T | AI | Temperature Sensor | BMS Contractor | DoO: AHU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0176 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-AMEN-3F | 3F | Return Air RH | AI | Humidity Sensor | BMS Contractor | DoO: AHU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0177 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-AMEN-3F | 3F | Supply Air T | AI | Temperature Sensor | BMS Contractor | DoO: AHU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0178 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-AMEN-3F | 3F | Return CO2 | AI | CO2 Sensor | BMS Contractor | DoO: AHU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0179 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-AMEN-3F | 3F | Fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: AHU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0180 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-AMEN-3F | 3F | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: AHU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0181 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-AMEN-3F | 3F | Fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: AHU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0182 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-AMEN-3F | 3F | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: AHU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0183 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-AMEN-3F | 3F | CHWS valve command | AO | Electric Valve Actuator | ME Contractor | DoO: AHU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0184 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-AMEN-3F | 3F | CHWS valve status | DI | Position Feedback | ME Contractor | DoO: AHU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0185 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-AMEN-3F | 3F | OA damper command | AO | Damper Actuator | ME Contractor | DoO: AHU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0186 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-AMEN-3F | 3F | RA damper command | AO | Damper Actuator | ME Contractor | DoO: AHU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0187 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-2F | 2F | Return Air T | AI | Temperature Sensor | BMS Contractor | DoO: AHU | PNL-BOH-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0188 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-2F | 2F | Return Air RH | AI | Humidity Sensor | BMS Contractor | DoO: AHU | PNL-BOH-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0189 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-2F | 2F | Supply Air T | AI | Temperature Sensor | BMS Contractor | DoO: AHU | PNL-BOH-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0190 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-2F | 2F | Return CO2 | AI | CO2 Sensor | BMS Contractor | DoO: AHU | PNL-BOH-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0191 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-2F | 2F | Fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: AHU | PNL-BOH-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0192 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-2F | 2F | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: AHU | PNL-BOH-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0193 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-2F | 2F | Fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: AHU | PNL-BOH-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0194 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-2F | 2F | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: AHU | PNL-BOH-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0195 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-2F | 2F | CHWS valve command | AO | Electric Valve Actuator | ME Contractor | DoO: AHU | PNL-BOH-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0196 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-2F | 2F | CHWS valve status | DI | Position Feedback | ME Contractor | DoO: AHU | PNL-BOH-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0197 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-2F | 2F | OA damper command | AO | Damper Actuator | ME Contractor | DoO: AHU | PNL-BOH-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0198 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-2F | 2F | RA damper command | AO | Damper Actuator | ME Contractor | DoO: AHU | PNL-BOH-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0199 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-BSMT | Basement | Return Air T | AI | Temperature Sensor | BMS Contractor | DoO: AHU | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0200 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-BSMT | Basement | Return Air RH | AI | Humidity Sensor | BMS Contractor | DoO: AHU | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0201 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-BSMT | Basement | Supply Air T | AI | Temperature Sensor | BMS Contractor | DoO: AHU | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0202 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-BSMT | Basement | Return CO2 | AI | CO2 Sensor | BMS Contractor | DoO: AHU | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0203 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-BSMT | Basement | Fan motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: AHU | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0204 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-BSMT | Basement | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier | DoO: AHU | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0205 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-BSMT | Basement | Fan VFD speed command | AO | VFD analog input | Equipment Supplier | DoO: AHU | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0206 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-BSMT | Basement | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier | DoO: AHU | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0207 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-BSMT | Basement | CHWS valve command | AO | Electric Valve Actuator | ME Contractor | DoO: AHU | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0208 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-BSMT | Basement | CHWS valve status | DI | Position Feedback | ME Contractor | DoO: AHU | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0209 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-BSMT | Basement | OA damper command | AO | Damper Actuator | ME Contractor | DoO: AHU | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0210 | VENT-AHU | AHU (Chilled-Water-Served) | AHU-BOH-BSMT | Basement | RA damper command | AO | Damper Actuator | ME Contractor | DoO: AHU | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0211 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.01 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0212 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.01 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0213 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.01 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0214 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.02 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0215 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.02 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0216 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.02 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0217 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.03 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0218 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.03 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0219 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.03 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0220 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.04 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0221 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.04 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0222 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.04 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0223 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.05 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0224 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.05 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0225 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.05 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0226 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.06 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0227 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.06 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0228 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.06 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0229 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.07 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0230 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.07 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0231 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.07 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0232 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.08 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0233 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.08 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0234 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.08 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0235 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.09 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0236 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.09 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0237 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.09 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0238 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.10 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0239 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.10 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0240 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.10 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0241 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.11 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0242 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.11 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0243 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.11 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0244 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.12 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0245 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.12 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0246 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.12 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0247 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.13 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0248 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.13 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0249 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.13 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0250 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.14 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0251 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.14 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0252 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.14 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0253 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.15 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0254 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.15 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0255 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.15 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0256 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.16 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0257 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.16 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0258 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.16 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0259 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.17 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0260 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.17 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0261 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.17 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0262 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.18 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0263 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.18 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0264 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.18 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0265 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.19 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0266 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.19 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0267 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.19 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0268 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.20 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0269 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.20 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0270 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.20 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0271 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.21 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0272 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.21 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0273 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.21 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0274 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.22 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0275 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.22 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0276 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.22 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0277 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.23 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0278 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.23 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0279 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.23 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0280 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.24 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0281 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.24 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0282 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.24 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0283 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.25 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0284 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.25 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0285 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.25 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0286 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.26 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0287 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.26 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0288 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.26 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0289 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.27 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0290 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.27 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0291 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.27 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0292 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.28 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0293 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.28 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0294 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.28 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0295 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.29 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0296 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.29 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0297 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.29 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0298 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.30 | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0299 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.30 | 3F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0300 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-3F.30 | 3F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0301 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.01 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0302 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.01 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0303 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.01 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0304 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.02 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0305 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.02 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0306 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.02 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0307 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.03 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0308 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.03 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0309 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.03 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0310 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.04 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0311 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.04 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0312 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.04 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0313 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.05 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0314 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.05 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0315 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.05 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0316 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.06 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0317 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.06 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0318 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.06 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0319 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.07 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0320 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.07 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0321 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.07 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0322 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.08 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0323 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.08 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0324 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.08 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0325 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.09 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0326 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.09 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0327 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.09 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0328 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.10 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0329 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.10 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0330 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.10 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0331 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.11 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0332 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.11 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0333 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.11 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0334 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.12 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0335 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.12 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0336 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.12 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0337 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.13 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0338 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.13 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0339 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.13 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0340 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.14 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0341 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.14 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0342 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.14 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0343 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.15 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0344 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.15 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0345 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.15 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0346 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.16 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0347 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.16 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0348 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.16 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0349 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.17 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0350 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.17 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0351 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.17 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0352 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.18 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0353 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.18 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0354 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.18 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0355 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.19 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0356 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.19 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0357 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.19 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0358 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.20 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0359 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.20 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0360 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.20 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0361 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.21 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0362 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.21 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0363 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.21 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0364 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.22 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0365 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.22 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0366 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.22 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0367 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.23 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0368 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.23 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0369 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.23 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0370 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.24 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0371 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.24 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0372 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.24 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0373 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.25 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0374 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.25 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0375 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.25 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0376 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.26 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0377 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.26 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0378 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.26 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0379 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.27 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0380 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.27 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0381 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.27 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0382 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.28 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0383 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.28 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0384 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.28 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0385 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.29 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0386 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.29 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0387 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.29 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0388 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.30 | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0389 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.30 | 2F | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0390 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-2F.30 | 2F | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0391 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.01 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0392 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.01 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0393 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.01 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0394 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.02 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0395 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.02 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0396 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.02 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0397 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.03 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0398 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.03 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0399 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.03 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0400 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.04 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0401 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.04 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0402 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.04 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0403 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.05 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0404 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.05 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0405 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.05 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0406 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.06 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0407 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.06 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0408 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.06 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0409 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.07 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0410 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.07 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0411 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.07 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0412 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.08 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0413 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.08 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0414 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.08 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0415 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.09 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0416 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.09 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0417 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.09 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0418 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.10 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0419 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.10 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0420 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.10 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0421 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.11 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0422 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.11 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0423 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.11 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0424 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.12 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0425 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.12 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0426 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.12 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0427 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.13 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0428 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.13 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0429 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.13 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0430 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.14 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0431 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.14 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0432 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.14 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0433 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.15 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0434 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.15 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0435 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.15 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0436 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.16 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0437 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.16 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0438 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.16 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0439 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.17 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0440 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.17 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0441 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.17 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0442 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.18 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0443 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.18 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0444 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.18 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0445 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.19 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0446 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.19 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0447 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.19 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0448 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.20 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0449 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.20 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0450 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.20 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0451 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.21 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0452 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.21 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0453 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.21 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0454 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.22 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0455 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.22 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0456 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.22 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0457 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.23 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0458 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.23 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0459 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.23 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0460 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.24 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0461 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.24 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0462 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.24 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0463 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.25 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0464 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.25 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0465 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.25 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0466 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.26 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0467 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.26 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0468 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.26 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0469 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.27 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0470 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.27 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0471 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.27 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0472 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.28 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0473 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.28 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0474 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.28 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0475 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.29 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0476 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.29 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0477 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.29 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0478 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.30 | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0479 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.30 | GF | Fan command | DO | Relay Output | Equipment Supplier | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0480 | VENT-FCU | FCU (guestroom/zone, hardwired) | FCU-GF.30 | GF | CHWS valve command (3-position) | DO | Valve Actuator | ME Contractor | DoO: FCU | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0481 | VENT-EAS | Exhaust Fan (General) | EAS-GF | GF | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: EAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0482 | VENT-EAS | Exhaust Fan (General) | EAS-GF | GF | Fan HOA | DI | Auxiliary Contact | Equipment Supplier | DoO: EAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0483 | VENT-EAS | Exhaust Fan (General) | EAS-GF | GF | Fan trip | DI | Auxiliary Contact | Equipment Supplier | DoO: EAS | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0484 | VENT-EAS | Exhaust Fan (General) | EAS-2F | 2F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: EAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0485 | VENT-EAS | Exhaust Fan (General) | EAS-2F | 2F | Fan HOA | DI | Auxiliary Contact | Equipment Supplier | DoO: EAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0486 | VENT-EAS | Exhaust Fan (General) | EAS-2F | 2F | Fan trip | DI | Auxiliary Contact | Equipment Supplier | DoO: EAS | PNL-2F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0487 | VENT-EAS | Exhaust Fan (General) | EAS-3F | 3F | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: EAS | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0488 | VENT-EAS | Exhaust Fan (General) | EAS-3F | 3F | Fan HOA | DI | Auxiliary Contact | Equipment Supplier | DoO: EAS | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0489 | VENT-EAS | Exhaust Fan (General) | EAS-3F | 3F | Fan trip | DI | Auxiliary Contact | Equipment Supplier | DoO: EAS | PNL-3F | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0490 | VENT-EAS | Exhaust Fan (General) | EAS-BSMT | Basement | Fan status | DI | Auxiliary Contact | Equipment Supplier | DoO: EAS | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0491 | VENT-EAS | Exhaust Fan (General) | EAS-BSMT | Basement | Fan HOA | DI | Auxiliary Contact | Equipment Supplier | DoO: EAS | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0492 | VENT-EAS | Exhaust Fan (General) | EAS-BSMT | Basement | Fan trip | DI | Auxiliary Contact | Equipment Supplier | DoO: EAS | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0493 | PL-Calorifiers | Calorifier (Hot Water Storage Tank) | CAL-1 | Plant Room | Tank temperature | AI | Temperature Sensor | BMS Contractor | DoO: Calorifier | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0494 | PL-Calorifiers | Calorifier (Hot Water Storage Tank) | CAL-2 | Plant Room | Tank temperature | AI | Temperature Sensor | BMS Contractor | DoO: Calorifier | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0495 | PL-Calorifiers | Calorifier (Hot Water Storage Tank) | CAL-3 | Plant Room | Tank temperature | AI | Temperature Sensor | BMS Contractor | DoO: Calorifier | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0496 | PL-Calorifiers | Calorifier (Hot Water Storage Tank) | CAL-4 | Plant Room | Tank temperature | AI | Temperature Sensor | BMS Contractor | DoO: Calorifier | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0497 | PL-Calorifiers | Calorifier (Hot Water Storage Tank) | CAL-5 | Plant Room | Tank temperature | AI | Temperature Sensor | BMS Contractor | DoO: Calorifier | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0498 | PL-Calorifiers | Calorifier (Hot Water Storage Tank) | CAL-6 | Plant Room | Tank temperature | AI | Temperature Sensor | BMS Contractor | DoO: Calorifier | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0499 | PL-HotWater | Hot Water Header Set | HDR-HW | Plant Room | HW Supply Header T | AI | Temperature Sensor | BMS Contractor | DoO: HW | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0500 | PL-HotWater | Hot Water Header Set | HDR-HW | Plant Room | HW Return Header T | AI | Temperature Sensor | BMS Contractor | DoO: HW | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0501 | PL-HotWater | Hot Water Header Set | HDR-HW | Plant Room | Make-up Cold Water T | AI | Temperature Sensor | BMS Contractor | DoO: HW | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0502 | PL-HotWater | Hot Water Header Set | HDR-HW | Plant Room | MUCW pressure | AI | Sensor | BMS Contractor | DoO: HW | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0503 | PL-HotWater | Hot Water Header Set | HDR-HW | Plant Room | HW circulating flow | AI | Sensor | BMS Contractor | DoO: HW | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0504 | PL-HotWater | Hot Water Header Set | HDR-HW | Plant Room | HW return T | AI | Temperature Sensor | BMS Contractor | DoO: HW | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0505 | PL-HeatPumps | Heat Pump | HP-1 | Plant Room | Pump motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: HP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0506 | PL-HeatPumps | Heat Pump | HP-1 | Plant Room | Pump HOA | DI | Auxiliary Contact | Equipment Supplier | DoO: HP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0507 | PL-HeatPumps | Heat Pump | HP-1 | Plant Room | Pump trip | DI | Auxiliary Contact | Equipment Supplier | DoO: HP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0508 | PL-HeatPumps | Heat Pump | HP-2 | Plant Room | Pump motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: HP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0509 | PL-HeatPumps | Heat Pump | HP-2 | Plant Room | Pump HOA | DI | Auxiliary Contact | Equipment Supplier | DoO: HP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0510 | PL-HeatPumps | Heat Pump | HP-2 | Plant Room | Pump trip | DI | Auxiliary Contact | Equipment Supplier | DoO: HP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0511 | PL-HeatPumps | Heat Pump | HP-3 | Plant Room | Pump motor status | DI | Auxiliary Contact | Equipment Supplier | DoO: HP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0512 | PL-HeatPumps | Heat Pump | HP-3 | Plant Room | Pump HOA | DI | Auxiliary Contact | Equipment Supplier | DoO: HP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0513 | PL-HeatPumps | Heat Pump | HP-3 | Plant Room | Pump trip | DI | Auxiliary Contact | Equipment Supplier | DoO: HP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0514 | PL-RecircPumps | Recirculating Pump | RP-1 | Plant Room | Pump status | DI | Auxiliary Contact | Equipment Supplier | DoO: RP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0515 | PL-RecircPumps | Recirculating Pump | RP-1 | Plant Room | Pump trip | DI | Auxiliary Contact | Equipment Supplier | DoO: RP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0516 | PL-RecircPumps | Recirculating Pump | RP-2 | Plant Room | Pump status | DI | Auxiliary Contact | Equipment Supplier | DoO: RP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0517 | PL-RecircPumps | Recirculating Pump | RP-2 | Plant Room | Pump trip | DI | Auxiliary Contact | Equipment Supplier | DoO: RP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0518 | PL-RecircPumps | Recirculating Pump | RP-3 | Plant Room | Pump status | DI | Auxiliary Contact | Equipment Supplier | DoO: RP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0519 | PL-RecircPumps | Recirculating Pump | RP-3 | Plant Room | Pump trip | DI | Auxiliary Contact | Equipment Supplier | DoO: RP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0520 | PL-RecircPumps | Recirculating Pump | RP-4 | Plant Room | Pump status | DI | Auxiliary Contact | Equipment Supplier | DoO: RP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0521 | PL-RecircPumps | Recirculating Pump | RP-4 | Plant Room | Pump trip | DI | Auxiliary Contact | Equipment Supplier | DoO: RP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0522 | PL-RecircPumps | Recirculating Pump | RP-5 | Plant Room | Pump status | DI | Auxiliary Contact | Equipment Supplier | DoO: RP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0523 | PL-RecircPumps | Recirculating Pump | RP-5 | Plant Room | Pump trip | DI | Auxiliary Contact | Equipment Supplier | DoO: RP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0524 | PL-RecircPumps | Recirculating Pump | RP-6 | Plant Room | Pump status | DI | Auxiliary Contact | Equipment Supplier | DoO: RP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0525 | PL-RecircPumps | Recirculating Pump | RP-6 | Plant Room | Pump trip | DI | Auxiliary Contact | Equipment Supplier | DoO: RP | PNL-CHPLANT-GND | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0526 | PL-Boiler | Steam Boiler | SB-1 | Basement | Steam pressure | AI | Steam Pressure Sensor (high-T) | BMS Contractor | DoO: Boiler | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0527 | PL-Boiler | Steam Boiler | SB-1 | Basement | Feedwater temperature | AI | Temperature Sensor | BMS Contractor | DoO: Boiler | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0528 | PL-Boiler | Steam Boiler | SB-1 | Basement | Fluegas temperature | AI | High-Temperature Sensor | BMS Contractor | DoO: Boiler | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0529 | PL-Boiler | Steam Boiler | SB-1 | Basement | Fluegas O2 | AI | Zirconia O2 Sensor | BMS Contractor | DoO: Boiler | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0530 | PL-Boiler | Steam Boiler | SB-1 | Basement | Blowdown valve command | AO | Motorized Blowdown Valve | BMS Contractor | DoO: Boiler | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0531 | PL-Boiler | Steam Boiler | SB-1 | Basement | Burner status | DI | Auxiliary Contact | Equipment Supplier | DoO: Boiler | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0532 | PL-Boiler | Steam Boiler | SB-1 | Basement | Burner trip | DI | Auxiliary Contact | Equipment Supplier | DoO: Boiler | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0533 | PL-Boiler | Steam Boiler | SB-1 | Basement | HOA status | DI | Auxiliary Contact | Equipment Supplier | DoO: Boiler | PNL-BSMT | MC Standards (ME/PL Points list) + project-specific equipment count per A-002
P0534 | Power-EE | Multifunction Power Meter (Main) | MTR-MAIN-1 | Main Switchgear | Modbus HLI (V/I/kW/kWh/PF/THD per phase) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0535 | Power-EE | Multifunction Power Meter (Main) | MTR-MAIN-2 | Main Switchgear | Modbus HLI (V/I/kW/kWh/PF/THD per phase) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0536 | Power-EE | Multifunction Power Meter (Main) | MTR-MAIN-3 | Main Switchgear | Modbus HLI (V/I/kW/kWh/PF/THD per phase) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0537 | Power-EE | Multifunction Power Meter (Feeder) | MTR-FDR-01 | Sub-Distribution Board | Modbus HLI (V/I/kW/kWh) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0538 | Power-EE | Multifunction Power Meter (Feeder) | MTR-FDR-02 | Sub-Distribution Board | Modbus HLI (V/I/kW/kWh) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0539 | Power-EE | Multifunction Power Meter (Feeder) | MTR-FDR-03 | Sub-Distribution Board | Modbus HLI (V/I/kW/kWh) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0540 | Power-EE | Multifunction Power Meter (Feeder) | MTR-FDR-04 | Sub-Distribution Board | Modbus HLI (V/I/kW/kWh) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0541 | Power-EE | Multifunction Power Meter (Feeder) | MTR-FDR-05 | Sub-Distribution Board | Modbus HLI (V/I/kW/kWh) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0542 | Power-EE | Multifunction Power Meter (Feeder) | MTR-FDR-06 | Sub-Distribution Board | Modbus HLI (V/I/kW/kWh) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0543 | Power-EE | Multifunction Power Meter (Feeder) | MTR-FDR-07 | Sub-Distribution Board | Modbus HLI (V/I/kW/kWh) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0544 | Power-EE | Multifunction Power Meter (Feeder) | MTR-FDR-08 | Sub-Distribution Board | Modbus HLI (V/I/kW/kWh) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0545 | Power-EE | Multifunction Power Meter (Feeder) | MTR-FDR-09 | Sub-Distribution Board | Modbus HLI (V/I/kW/kWh) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0546 | Power-EE | Multifunction Power Meter (Feeder) | MTR-FDR-10 | Sub-Distribution Board | Modbus HLI (V/I/kW/kWh) | HLI | Modbus Power Meter | BMS Contractor | Energy reporting | PNL-GF | MC Standards (ME/PL Points list) + project-specific equipment count per A-002 | Modbus RTU
P0547 | Network | BMS Network Drop | NET-PNL-RD | panel | BACnet/IP drop at PNL-RD | Network | RJ45 + Cat6 to edge switch | BMS Contractor | DoO: Network | PNL-RD | A5 architecture
P0548 | Network | BMS Network Drop | NET-PNL-3F | panel | BACnet/IP drop at PNL-3F | Network | RJ45 + Cat6 to edge switch | BMS Contractor | DoO: Network | PNL-3F | A5 architecture
P0549 | Network | BMS Network Drop | NET-PNL-2F | panel | BACnet/IP drop at PNL-2F | Network | RJ45 + Cat6 to edge switch | BMS Contractor | DoO: Network | PNL-2F | A5 architecture
P0550 | Network | BMS Network Drop | NET-PNL-GF | panel | BACnet/IP drop at PNL-GF | Network | RJ45 + Cat6 to edge switch | BMS Contractor | DoO: Network | PNL-GF | A5 architecture
P0551 | Network | BMS Network Drop | NET-PNL-BSMT | panel | BACnet/IP drop at PNL-BSMT | Network | RJ45 + Cat6 to edge switch | BMS Contractor | DoO: Network | PNL-BSMT | A5 architecture
P0552 | Network | BMS Network Drop | NET-PNL-CHPLANT-GND | panel | BACnet/IP drop at PNL-CHPLANT-GND | Network | RJ45 + Cat6 to edge switch | BMS Contractor | DoO: Network | PNL-CHPLANT-GND | A5 architecture
P0553 | Network | BMS Network Drop | NET-PNL-BOH-2F | panel | BACnet/IP drop at PNL-BOH-2F | Network | RJ45 + Cat6 to edge switch | BMS Contractor | DoO: Network | PNL-BOH-2F | A5 architecture
P0554 | Network | BMS Network Drop | NET-PNL-HE-GF | panel | BACnet/IP drop at PNL-HE-GF | Network | RJ45 + Cat6 to edge switch | BMS Contractor | DoO: Network | PNL-HE-GF | A5 architecture