## Summary
A3 — Cable Schedule Summary
Total field cable runs | 258
Total field cable length (m) | 6864
Total trunk cable length (m) | 485
Total power feed length (m) | 96
GRAND TOTAL cable length (m) | 7445
By cable type (m)
4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 3245
4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 2830
4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 552
Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 237

## Field Cables
ID | From | To | Equipment Class | System | Location | Cable Type | Conductors Required | Conductors Specified | Length (m) | I/O Points Carried | Notes
C0001 | PNL-3F | AHU-AMEN-3F (BMS Contractor) | AHU (Chilled-Water-Served) | VENT-AHU | 3F | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 35 | 4 | 4 I/O points carried, 6C cable; length 35 m (typical_range:same_floor_corridor_field)
C0002 | PNL-3F | AHU-AMEN-3F (Equipment Supplier) | AHU (Chilled-Water-Served) | VENT-AHU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 35 | 4 | 4 I/O points carried, 4C cable; length 35 m (typical_range:same_floor_corridor_field)
C0003 | PNL-3F | AHU-AMEN-3F (ME Contractor) | AHU (Chilled-Water-Served) | VENT-AHU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 35 | 4 | 4 I/O points carried, 6C cable; length 35 m (typical_range:same_floor_corridor_field)
C0004 | PNL-2F | AHU-BALL-2F (BMS Contractor) | AHU (Chilled-Water-Served) | VENT-AHU | 2F | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 35 | 4 | 4 I/O points carried, 6C cable; length 35 m (typical_range:same_floor_corridor_field)
C0005 | PNL-2F | AHU-BALL-2F (Equipment Supplier) | AHU (Chilled-Water-Served) | VENT-AHU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 35 | 4 | 4 I/O points carried, 4C cable; length 35 m (typical_range:same_floor_corridor_field)
C0006 | PNL-2F | AHU-BALL-2F (ME Contractor) | AHU (Chilled-Water-Served) | VENT-AHU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 35 | 4 | 4 I/O points carried, 6C cable; length 35 m (typical_range:same_floor_corridor_field)
C0007 | PNL-BOH-2F | AHU-BOH-2F (BMS Contractor) | AHU (Chilled-Water-Served) | VENT-AHU | 2F | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 32 | 4 | 4 I/O points carried, 6C cable; length 32 m (typical_range:boh_corridor_field)
C0008 | PNL-BOH-2F | AHU-BOH-2F (Equipment Supplier) | AHU (Chilled-Water-Served) | VENT-AHU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 32 | 4 | 4 I/O points carried, 4C cable; length 32 m (typical_range:boh_corridor_field)
C0009 | PNL-BOH-2F | AHU-BOH-2F (ME Contractor) | AHU (Chilled-Water-Served) | VENT-AHU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 32 | 4 | 4 I/O points carried, 6C cable; length 32 m (typical_range:boh_corridor_field)
C0010 | PNL-BSMT | AHU-BOH-BSMT (BMS Contractor) | AHU (Chilled-Water-Served) | VENT-AHU | Basement | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 32 | 4 | 4 I/O points carried, 6C cable; length 32 m (typical_range:boh_corridor_field)
C0011 | PNL-BSMT | AHU-BOH-BSMT (Equipment Supplier) | AHU (Chilled-Water-Served) | VENT-AHU | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 32 | 4 | 4 I/O points carried, 4C cable; length 32 m (typical_range:boh_corridor_field)
C0012 | PNL-BSMT | AHU-BOH-BSMT (ME Contractor) | AHU (Chilled-Water-Served) | VENT-AHU | Basement | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 32 | 4 | 4 I/O points carried, 6C cable; length 32 m (typical_range:boh_corridor_field)
C0013 | PNL-GF | AHU-LOBBY-GF (BMS Contractor) | AHU (Chilled-Water-Served) | VENT-AHU | GF | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 35 | 4 | 4 I/O points carried, 6C cable; length 35 m (typical_range:same_floor_corridor_field)
C0014 | PNL-GF | AHU-LOBBY-GF (Equipment Supplier) | AHU (Chilled-Water-Served) | VENT-AHU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 35 | 4 | 4 I/O points carried, 4C cable; length 35 m (typical_range:same_floor_corridor_field)
C0015 | PNL-GF | AHU-LOBBY-GF (ME Contractor) | AHU (Chilled-Water-Served) | VENT-AHU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 35 | 4 | 4 I/O points carried, 6C cable; length 35 m (typical_range:same_floor_corridor_field)
C0016 | PNL-2F | AHU-REST-2F (BMS Contractor) | AHU (Chilled-Water-Served) | VENT-AHU | 2F | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 35 | 4 | 4 I/O points carried, 6C cable; length 35 m (typical_range:same_floor_corridor_field)
C0017 | PNL-2F | AHU-REST-2F (Equipment Supplier) | AHU (Chilled-Water-Served) | VENT-AHU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 35 | 4 | 4 I/O points carried, 4C cable; length 35 m (typical_range:same_floor_corridor_field)
C0018 | PNL-2F | AHU-REST-2F (ME Contractor) | AHU (Chilled-Water-Served) | VENT-AHU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 5 | 6 | 35 | 4 | 4 I/O points carried, 6C cable; length 35 m (typical_range:same_floor_corridor_field)
C0019 | PNL-CHPLANT-GND | CAL-1 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | PL-Calorifiers | Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0020 | PNL-CHPLANT-GND | CAL-2 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | PL-Calorifiers | Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0021 | PNL-CHPLANT-GND | CAL-3 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | PL-Calorifiers | Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0022 | PNL-CHPLANT-GND | CAL-4 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | PL-Calorifiers | Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0023 | PNL-CHPLANT-GND | CAL-5 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | PL-Calorifiers | Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0024 | PNL-CHPLANT-GND | CAL-6 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | PL-Calorifiers | Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0025 | PNL-CHPLANT-GND | CHWP-1.1 (Equipment Supplier) | Primary CHW Pump | HVAC-Pumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0026 | PNL-CHPLANT-GND | CHWP-1.2 (Equipment Supplier) | Primary CHW Pump | HVAC-Pumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0027 | PNL-CHPLANT-GND | CHWP-1.3 (Equipment Supplier) | Primary CHW Pump | HVAC-Pumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0028 | PNL-CHPLANT-GND | CHWP-1.STBY (Equipment Supplier) | Primary CHW Pump (Standby) | HVAC-Pumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0029 | PNL-CHPLANT-GND | COWP-1 (Equipment Supplier) | Condenser Water Pump | HVAC-Pumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0030 | PNL-CHPLANT-GND | COWP-2 (Equipment Supplier) | Condenser Water Pump | HVAC-Pumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0031 | PNL-CHPLANT-GND | COWP-3 (Equipment Supplier) | Condenser Water Pump | HVAC-Pumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0032 | PNL-RD | CT-1 (BMS Contractor) | Cooling Tower | HVAC-Cooling-Towers | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 1 | 4 | 18 | 1 | 1 I/O points carried, 4C cable; length 18 m (typical_range:roofdeck_same_area)
C0033 | PNL-RD | CT-1 (Equipment Supplier) | Cooling Tower | HVAC-Cooling-Towers | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 18 | 5 | 5 I/O points carried, 6C cable; length 18 m (typical_range:roofdeck_same_area)
C0034 | PNL-RD | CT-2 (BMS Contractor) | Cooling Tower | HVAC-Cooling-Towers | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 1 | 4 | 18 | 1 | 1 I/O points carried, 4C cable; length 18 m (typical_range:roofdeck_same_area)
C0035 | PNL-RD | CT-2 (Equipment Supplier) | Cooling Tower | HVAC-Cooling-Towers | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 18 | 5 | 5 I/O points carried, 6C cable; length 18 m (typical_range:roofdeck_same_area)
C0036 | PNL-RD | CT-3 (BMS Contractor) | Cooling Tower | HVAC-Cooling-Towers | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 1 | 4 | 18 | 1 | 1 I/O points carried, 4C cable; length 18 m (typical_range:roofdeck_same_area)
C0037 | PNL-RD | CT-3 (Equipment Supplier) | Cooling Tower | HVAC-Cooling-Towers | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 18 | 5 | 5 I/O points carried, 6C cable; length 18 m (typical_range:roofdeck_same_area)
C0038 | PNL-RD | CT-COMMON (BMS Contractor) | Cooling Tower (Common) | HVAC-Cooling-Towers | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 2 | 4 | 18 | 2 | 2 I/O points carried, 4C cable; length 18 m (typical_range:roofdeck_same_area)
C0039 | PNL-2F | DOAS-2F (BMS Contractor) | DOAS Unit | VENT-DOAS | 2F | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 35 | 5 | 5 I/O points carried, 6C cable; length 35 m (typical_range:same_floor_corridor_field)
C0040 | PNL-2F | DOAS-2F (Equipment Supplier) | DOAS Unit | VENT-DOAS | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 14 | 16 | 35 | 12 | 12 I/O points carried, 16C cable; length 35 m (typical_range:same_floor_corridor_field)
C0041 | PNL-2F | DOAS-2F (ME Contractor) | DOAS Unit | VENT-DOAS | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 35 | 4 | 4 I/O points carried, 4C cable; length 35 m (typical_range:same_floor_corridor_field)
C0042 | PNL-GF | DOAS-GF (BMS Contractor) | DOAS Unit | VENT-DOAS | GF | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 35 | 5 | 5 I/O points carried, 6C cable; length 35 m (typical_range:same_floor_corridor_field)
C0043 | PNL-GF | DOAS-GF (Equipment Supplier) | DOAS Unit | VENT-DOAS | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 14 | 16 | 35 | 12 | 12 I/O points carried, 16C cable; length 35 m (typical_range:same_floor_corridor_field)
C0044 | PNL-GF | DOAS-GF (ME Contractor) | DOAS Unit | VENT-DOAS | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 35 | 4 | 4 I/O points carried, 4C cable; length 35 m (typical_range:same_floor_corridor_field)
C0045 | PNL-RD | DOAS-RD (BMS Contractor) | DOAS Unit | VENT-DOAS | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 18 | 5 | 5 I/O points carried, 6C cable; length 18 m (typical_range:roofdeck_same_area)
C0046 | PNL-RD | DOAS-RD (Equipment Supplier) | DOAS Unit | VENT-DOAS | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 14 | 16 | 18 | 12 | 12 I/O points carried, 16C cable; length 18 m (typical_range:roofdeck_same_area)
C0047 | PNL-RD | DOAS-RD (ME Contractor) | DOAS Unit | VENT-DOAS | Roofdeck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 18 | 4 | 4 I/O points carried, 4C cable; length 18 m (typical_range:roofdeck_same_area)
C0048 | PNL-2F | EAS-2F (Equipment Supplier) | Exhaust Fan (General) | VENT-EAS | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:same_floor_corridor_field)
C0049 | PNL-3F | EAS-3F (Equipment Supplier) | Exhaust Fan (General) | VENT-EAS | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:same_floor_corridor_field)
C0050 | PNL-BSMT | EAS-BSMT (Equipment Supplier) | Exhaust Fan (General) | VENT-EAS | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 3 | 4 | 32 | 3 | 3 I/O points carried, 4C cable; length 32 m (typical_range:boh_corridor_field)
C0051 | PNL-GF | EAS-GF (Equipment Supplier) | Exhaust Fan (General) | VENT-EAS | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:same_floor_corridor_field)
C0052 | PNL-2F | FCU-2F.01 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0053 | PNL-2F | FCU-2F.01 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0054 | PNL-2F | FCU-2F.02 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0055 | PNL-2F | FCU-2F.02 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0056 | PNL-2F | FCU-2F.03 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0057 | PNL-2F | FCU-2F.03 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0058 | PNL-2F | FCU-2F.04 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0059 | PNL-2F | FCU-2F.04 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0060 | PNL-2F | FCU-2F.05 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0061 | PNL-2F | FCU-2F.05 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0062 | PNL-2F | FCU-2F.06 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0063 | PNL-2F | FCU-2F.06 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0064 | PNL-2F | FCU-2F.07 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0065 | PNL-2F | FCU-2F.07 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0066 | PNL-2F | FCU-2F.08 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0067 | PNL-2F | FCU-2F.08 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0068 | PNL-2F | FCU-2F.09 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0069 | PNL-2F | FCU-2F.09 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0070 | PNL-2F | FCU-2F.10 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0071 | PNL-2F | FCU-2F.10 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0072 | PNL-2F | FCU-2F.11 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0073 | PNL-2F | FCU-2F.11 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0074 | PNL-2F | FCU-2F.12 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0075 | PNL-2F | FCU-2F.12 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0076 | PNL-2F | FCU-2F.13 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0077 | PNL-2F | FCU-2F.13 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0078 | PNL-2F | FCU-2F.14 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0079 | PNL-2F | FCU-2F.14 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0080 | PNL-2F | FCU-2F.15 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0081 | PNL-2F | FCU-2F.15 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0082 | PNL-2F | FCU-2F.16 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0083 | PNL-2F | FCU-2F.16 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0084 | PNL-2F | FCU-2F.17 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0085 | PNL-2F | FCU-2F.17 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0086 | PNL-2F | FCU-2F.18 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0087 | PNL-2F | FCU-2F.18 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0088 | PNL-2F | FCU-2F.19 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0089 | PNL-2F | FCU-2F.19 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0090 | PNL-2F | FCU-2F.20 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0091 | PNL-2F | FCU-2F.20 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0092 | PNL-2F | FCU-2F.21 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0093 | PNL-2F | FCU-2F.21 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0094 | PNL-2F | FCU-2F.22 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0095 | PNL-2F | FCU-2F.22 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0096 | PNL-2F | FCU-2F.23 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0097 | PNL-2F | FCU-2F.23 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0098 | PNL-2F | FCU-2F.24 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0099 | PNL-2F | FCU-2F.24 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0100 | PNL-2F | FCU-2F.25 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0101 | PNL-2F | FCU-2F.25 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0102 | PNL-2F | FCU-2F.26 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0103 | PNL-2F | FCU-2F.26 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0104 | PNL-2F | FCU-2F.27 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0105 | PNL-2F | FCU-2F.27 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0106 | PNL-2F | FCU-2F.28 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0107 | PNL-2F | FCU-2F.28 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0108 | PNL-2F | FCU-2F.29 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0109 | PNL-2F | FCU-2F.29 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0110 | PNL-2F | FCU-2F.30 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0111 | PNL-2F | FCU-2F.30 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 2F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0112 | PNL-3F | FCU-3F.01 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0113 | PNL-3F | FCU-3F.01 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0114 | PNL-3F | FCU-3F.02 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0115 | PNL-3F | FCU-3F.02 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0116 | PNL-3F | FCU-3F.03 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0117 | PNL-3F | FCU-3F.03 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0118 | PNL-3F | FCU-3F.04 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0119 | PNL-3F | FCU-3F.04 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0120 | PNL-3F | FCU-3F.05 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0121 | PNL-3F | FCU-3F.05 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0122 | PNL-3F | FCU-3F.06 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0123 | PNL-3F | FCU-3F.06 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0124 | PNL-3F | FCU-3F.07 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0125 | PNL-3F | FCU-3F.07 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0126 | PNL-3F | FCU-3F.08 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0127 | PNL-3F | FCU-3F.08 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0128 | PNL-3F | FCU-3F.09 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0129 | PNL-3F | FCU-3F.09 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0130 | PNL-3F | FCU-3F.10 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0131 | PNL-3F | FCU-3F.10 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0132 | PNL-3F | FCU-3F.11 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0133 | PNL-3F | FCU-3F.11 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0134 | PNL-3F | FCU-3F.12 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0135 | PNL-3F | FCU-3F.12 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0136 | PNL-3F | FCU-3F.13 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0137 | PNL-3F | FCU-3F.13 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0138 | PNL-3F | FCU-3F.14 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0139 | PNL-3F | FCU-3F.14 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0140 | PNL-3F | FCU-3F.15 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0141 | PNL-3F | FCU-3F.15 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0142 | PNL-3F | FCU-3F.16 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0143 | PNL-3F | FCU-3F.16 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0144 | PNL-3F | FCU-3F.17 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0145 | PNL-3F | FCU-3F.17 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0146 | PNL-3F | FCU-3F.18 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0147 | PNL-3F | FCU-3F.18 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0148 | PNL-3F | FCU-3F.19 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0149 | PNL-3F | FCU-3F.19 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0150 | PNL-3F | FCU-3F.20 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0151 | PNL-3F | FCU-3F.20 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0152 | PNL-3F | FCU-3F.21 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0153 | PNL-3F | FCU-3F.21 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0154 | PNL-3F | FCU-3F.22 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0155 | PNL-3F | FCU-3F.22 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0156 | PNL-3F | FCU-3F.23 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0157 | PNL-3F | FCU-3F.23 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0158 | PNL-3F | FCU-3F.24 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0159 | PNL-3F | FCU-3F.24 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0160 | PNL-3F | FCU-3F.25 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0161 | PNL-3F | FCU-3F.25 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0162 | PNL-3F | FCU-3F.26 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0163 | PNL-3F | FCU-3F.26 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0164 | PNL-3F | FCU-3F.27 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0165 | PNL-3F | FCU-3F.27 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0166 | PNL-3F | FCU-3F.28 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0167 | PNL-3F | FCU-3F.28 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0168 | PNL-3F | FCU-3F.29 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0169 | PNL-3F | FCU-3F.29 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0170 | PNL-3F | FCU-3F.30 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0171 | PNL-3F | FCU-3F.30 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | 3F | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0172 | PNL-GF | FCU-GF.01 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0173 | PNL-GF | FCU-GF.01 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0174 | PNL-GF | FCU-GF.02 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0175 | PNL-GF | FCU-GF.02 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0176 | PNL-GF | FCU-GF.03 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0177 | PNL-GF | FCU-GF.03 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0178 | PNL-GF | FCU-GF.04 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0179 | PNL-GF | FCU-GF.04 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0180 | PNL-GF | FCU-GF.05 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0181 | PNL-GF | FCU-GF.05 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0182 | PNL-GF | FCU-GF.06 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0183 | PNL-GF | FCU-GF.06 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0184 | PNL-GF | FCU-GF.07 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0185 | PNL-GF | FCU-GF.07 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0186 | PNL-GF | FCU-GF.08 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0187 | PNL-GF | FCU-GF.08 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0188 | PNL-GF | FCU-GF.09 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0189 | PNL-GF | FCU-GF.09 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0190 | PNL-GF | FCU-GF.10 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0191 | PNL-GF | FCU-GF.10 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0192 | PNL-GF | FCU-GF.11 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0193 | PNL-GF | FCU-GF.11 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0194 | PNL-GF | FCU-GF.12 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0195 | PNL-GF | FCU-GF.12 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0196 | PNL-GF | FCU-GF.13 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0197 | PNL-GF | FCU-GF.13 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0198 | PNL-GF | FCU-GF.14 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0199 | PNL-GF | FCU-GF.14 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0200 | PNL-GF | FCU-GF.15 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0201 | PNL-GF | FCU-GF.15 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0202 | PNL-GF | FCU-GF.16 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0203 | PNL-GF | FCU-GF.16 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0204 | PNL-GF | FCU-GF.17 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0205 | PNL-GF | FCU-GF.17 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0206 | PNL-GF | FCU-GF.18 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0207 | PNL-GF | FCU-GF.18 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0208 | PNL-GF | FCU-GF.19 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0209 | PNL-GF | FCU-GF.19 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0210 | PNL-GF | FCU-GF.20 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0211 | PNL-GF | FCU-GF.20 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0212 | PNL-GF | FCU-GF.21 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0213 | PNL-GF | FCU-GF.21 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0214 | PNL-GF | FCU-GF.22 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0215 | PNL-GF | FCU-GF.22 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0216 | PNL-GF | FCU-GF.23 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0217 | PNL-GF | FCU-GF.23 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0218 | PNL-GF | FCU-GF.24 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0219 | PNL-GF | FCU-GF.24 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0220 | PNL-GF | FCU-GF.25 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0221 | PNL-GF | FCU-GF.25 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0222 | PNL-GF | FCU-GF.26 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0223 | PNL-GF | FCU-GF.26 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0224 | PNL-GF | FCU-GF.27 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0225 | PNL-GF | FCU-GF.27 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0226 | PNL-GF | FCU-GF.28 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0227 | PNL-GF | FCU-GF.28 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0228 | PNL-GF | FCU-GF.29 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0229 | PNL-GF | FCU-GF.29 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0230 | PNL-GF | FCU-GF.30 (Equipment Supplier) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 28 | 2 | 2 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0231 | PNL-GF | FCU-GF.30 (ME Contractor) | FCU (guestroom/zone, hardwired) | VENT-FCU | GF | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:guestroom_zone_field)
C0232 | PNL-CHPLANT-GND | HDR-CHW-BP (BMS Contractor) | CHW Bypass Header | HVAC-Chillers | Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0233 | PNL-CHPLANT-GND | HDR-CHWR (BMS Contractor) | CHW Return Main Header | HVAC-Chillers | Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0234 | PNL-CHPLANT-GND | HDR-CHWS (BMS Contractor) | CHW Supply Main Header | HVAC-Chillers | Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0235 | PNL-RD | HDR-COW (BMS Contractor) | Condenser Water Header | HVAC-Chillers | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 18 | 3 | 3 I/O points carried, 4C cable; length 18 m (typical_range:roofdeck_same_area)
C0236 | PNL-CHPLANT-GND | HDR-HW (BMS Contractor) | Hot Water Header Set | PL-HotWater | Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 12 | 6 | 6 I/O points carried, 8C cable; length 12 m (typical_range:plant_room_same_room)
C0237 | PNL-CHPLANT-GND | HP-1 (Equipment Supplier) | Heat Pump | PL-HeatPumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0238 | PNL-CHPLANT-GND | HP-2 (Equipment Supplier) | Heat Pump | PL-HeatPumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0239 | PNL-CHPLANT-GND | HP-3 (Equipment Supplier) | Heat Pump | PL-HeatPumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0240 | PNL-RD | PAHU-RD (BMS Contractor) | Precooled Air Handling Unit | VENT-PAHU | Roofdeck | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 18 | 3 | 3 I/O points carried, 4C cable; length 18 m (typical_range:roofdeck_same_area)
C0241 | PNL-RD | PAHU-RD (Equipment Supplier) | Precooled Air Handling Unit | VENT-PAHU | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 18 | 5 | 5 I/O points carried, 6C cable; length 18 m (typical_range:roofdeck_same_area)
C0242 | PNL-RD | PAHU-RD (ME Contractor) | Precooled Air Handling Unit | VENT-PAHU | Roofdeck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 2 | 4 | 18 | 2 | 2 I/O points carried, 4C cable; length 18 m (typical_range:roofdeck_same_area)
C0243 | PNL-CHPLANT-GND | RP-1 (Equipment Supplier) | Recirculating Pump | PL-RecircPumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0244 | PNL-CHPLANT-GND | RP-2 (Equipment Supplier) | Recirculating Pump | PL-RecircPumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0245 | PNL-CHPLANT-GND | RP-3 (Equipment Supplier) | Recirculating Pump | PL-RecircPumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0246 | PNL-CHPLANT-GND | RP-4 (Equipment Supplier) | Recirculating Pump | PL-RecircPumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0247 | PNL-CHPLANT-GND | RP-5 (Equipment Supplier) | Recirculating Pump | PL-RecircPumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0248 | PNL-CHPLANT-GND | RP-6 (Equipment Supplier) | Recirculating Pump | PL-RecircPumps | Plant Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0249 | PNL-BSMT | SB-1 (BMS Contractor) | Steam Boiler | PL-Boiler | Basement | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 32 | 5 | 5 I/O points carried, 6C cable; length 32 m (typical_range:boh_corridor_field)
C0250 | PNL-BSMT | SB-1 (Equipment Supplier) | Steam Boiler | PL-Boiler | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 3 | 4 | 32 | 3 | 3 I/O points carried, 4C cable; length 32 m (typical_range:boh_corridor_field)
C0251 | PNL-RD | NET-PNL-RD (Network) | BMS Network Drop | Network | panel | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 18 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 18 m (typical_range:roofdeck_same_area)
C0252 | PNL-3F | NET-PNL-3F (Network) | BMS Network Drop | Network | panel | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 35 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 35 m (typical_range:same_floor_corridor_field)
C0253 | PNL-2F | NET-PNL-2F (Network) | BMS Network Drop | Network | panel | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 35 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 35 m (typical_range:same_floor_corridor_field)
C0254 | PNL-GF | NET-PNL-GF (Network) | BMS Network Drop | Network | panel | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 35 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 35 m (typical_range:same_floor_corridor_field)
C0255 | PNL-BSMT | NET-PNL-BSMT (Network) | BMS Network Drop | Network | panel | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 35 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 35 m (typical_range:same_floor_corridor_field)
C0256 | PNL-CHPLANT-GND | NET-PNL-CHPLANT-GND (Network) | BMS Network Drop | Network | panel | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0257 | PNL-BOH-2F | NET-PNL-BOH-2F (Network) | BMS Network Drop | Network | panel | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 32 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 32 m (typical_range:boh_corridor_field)
C0258 | PNL-HE-GF | NET-PNL-HE-GF (Network) | BMS Network Drop | Network | panel | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 35 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 35 m (typical_range:same_floor_corridor_field)

## Trunks
ID | From | To | Cable Type | Length (m) | Notes
T0259 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for 2nd Floor — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0260 | BMS Server Room (head-end) | All BMS panels at Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Basement — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0261 | BMS Server Room (head-end) | All BMS panels at Roofdeck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Roofdeck — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0262 | BMS Server Room (head-end) | BMS panel controllers (per topology id mstp_main_backbone) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 245 | Backbone routed from PNL-CHPLANT-GND through PNL-BSMT → PNL-HE-GF → PNL-GF → PNL-BOH-2F → PNL-2F → PNL-3F → PNL-RD. 7 inter-panel hops; mix of intra-floor and inter-floor segments. Total length applied below.

## Panel Power Feeds
ID | From | To | Cable Type | Length (m) | Notes
P0263 | Local panelboard / EE-supplied feeder | PNL-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 12 m (typical_range:plant_room_same_room)
P0264 | Local panelboard / EE-supplied feeder | PNL-3F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 12 m (typical_range:plant_room_same_room)
P0265 | Local panelboard / EE-supplied feeder | PNL-BOH-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 12 m (typical_range:plant_room_same_room)
P0266 | Local panelboard / EE-supplied feeder | PNL-BSMT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 12 m (typical_range:plant_room_same_room)
P0267 | Local panelboard / EE-supplied feeder | PNL-CHPLANT-GND — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 12 m (typical_range:plant_room_same_room)
P0268 | Local panelboard / EE-supplied feeder | PNL-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 12 m (typical_range:plant_room_same_room)
P0269 | Local panelboard / EE-supplied feeder | PNL-HE-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 12 m (typical_range:plant_room_same_room)
P0270 | Local panelboard / EE-supplied feeder | PNL-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 12 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 12 m (typical_range:plant_room_same_room)