Table of Contents

# 08 — Customer Clarifications (RFI List)

This proposal is based on the documents you provided. The items below would refine pricing and schedule. Items marked P1 materially affect price; please prioritize those.

## Cover note

In preparing our proposal for the Kingsford Hotel Bacolod BMS, we identified the items below as needing clarification. Items marked P1 materially affect pricing and schedule and should be answered first. Each question states the default we have used in our base proposal; your answers refine the proposal and may reduce contingency.

## Open items

| ID | Priority | Discipline | Question | Default in proposal | Affects |
| --- | --- | --- | --- | --- | --- |
| Q-001 | P1 | TECH-ME | Confirm full list of BMS-monitored systems for this hotel. Are all Megaworld MC Standards systems (ME + PL) in scope, or a sub-set? | Full MC Standards systems for the floors covered by the BMS-01..04 sheets | A1, A2, BOQ |
| Q-005 | P1 | OWNER | Are guestroom-level HVAC controls (FCU per guestroom) in BMS scope, or part of a separate fit-out / owner package? | In scope at typical density (sample floors only — not per-room) | A1, A2, A3, BOQ |
| Q-007 | P1 | PROJECT | What is the required completion date / project duration? | 16 weeks PO → handover | D1, D2, mobilization |
| Q-018 | P1 | PROJECT | The cover letter says “Rehabilitation” but the technical drawings are Construction Bulletins (new construction). Confirm classification. | Greenfield (per technical docs) | Whole proposal |
| Q-012 | P2 | TECH-IT | Is integration with FDAS, PMS, CCTV, or ACS required in this scope? | None in base scope; each available as Option (PHP 200–500K) | 7.x options |
| Q-013 | P2 | OWNER | Confirm acceptable BMS brand list. Default: Siemens (Desigo PXC / Desigo CC / 7KM PAC) for BMS components and Dell PowerEdge / OptiPlex / Precision for head-end PCs. | Per default brand standards | A2, A6, BOQ |
| Q-014 | P2 | COMMERCIAL | Confirm payment terms, retention %, taxes, currency. | PHP, 12% VAT, retention 10%, milestone-based payment | 06 commercial summary |
| Q-015 | P2 | OWNER | Operator training duration and number of attendees. | 16 hours, 2 days, up to 6 operators | 6.0 |
| Q-016 | P3 | OWNER | Is a 1-year preventive-maintenance contract requested with this proposal? | Optional, priced separately | 7.1 |
| Q-002 | P2 | TECH-EE | EE Plan was provided as a Construction Bulletin set (raster). Provide CAD or scaled PDF for cable-route measurement at shop-drawing stage. | Lengths use reasoned typical-ranges per A3-route-lengths.yaml | A3 |
| Q-003 | P2 | TECH-ME | Provide architectural floor plans (corridors, ceiling voids, riser shafts) for cable-route measurement. | Same as above | A3 |
| Q-004 | P3 | TECH-EE | Confirm panel-board IDs and circuit assignments for the 25 dedicated 240V single-phase circuits to BMS panels and the head-end UPS. | Per A7 schedule (placeholder circuit IDs) | A7 |
| Q-006 | P3 | TECH-IT | Confirm whether the BMS uplink lands on a dedicated VLAN on the customer LAN or remains fully isolated. | Isolated LAN with single uplink | A5 |
| Q-008 | P2 | TECH-ME | Per-guestroom FCU count per floor — confirm number of guestrooms per typical floor and zoning approach. | Sample 3 floors × 30 FCU/floor at typical density | A2, A3 |
| Q-009 | P3 | TECH-ME | Smoke control / kitchen exhaust interlocks — in BMS scope? | Status monitoring only; no automated suppression interlock | A1 |
| Q-010 | P3 | OWNER | Energy-savings algorithms required (chiller plant sequencing, demand control, peak shaving)? | Pre-engineered set included | B1 |
| Q-011 | P3 | OWNER | Number of BMS administrator (vs. operator) seats; remote-access required? | 1 admin, 2 operator workstations, 1 graphics PC; no remote access in base scope | A6 |
| Q-017 | P3 | COMMERCIAL | Confirm warranty period. | 1 year on workmanship + 1 year on equipment per supplier warranty | 6.4 |
| Q-019 | P3 | TECH-EE | Power-meter scope: confirm number and class (main vs. sub-feeder). | 3 main + 10 sub-feeder = 13 meters | A2, 2.6 |
| Q-020 | P3 | TECH-ME | Confirm number of BTU meters and chiller-side BACnet integration availability. | 1 plant-level BTU meter; chillers have BACnet IP cards (per typical) | A2 |

Total: 19 active questions (4 P1, 9 P2, 6 P3).