Table of Contents

# Internal Team Notes — 2026-04-kingsford-bms-AB3

Audience: the proposal team running the next pass on this project.

This document compiles actionable items pulled from the project’s working artifacts. Each section is what to do next — verify, refine, or reconsider — to improve the proposal before it goes to the customer or as part of an RFQ-response cycle.

Sources compiled:

- 07-assumptions.md — assumptions to verify or refine

- 08-customer-clarifications.md — questions to send the customer

- 99-decision-log.md — decisions worth revisiting

- 03-doc-inventory.md — gap analysis on customer inputs

- 05-working-docs/A3-cable-schedule.yaml — cable-length fallbacks to verify

- 05-working-docs/D3-risk-register.md — project risks (if present)

- 09-rfq-package/ — RFQ packages (cost-reduction via competitive bidding)

## 1. Customer clarifications (RFI list)

20 open questions to send the customer. Each has a documented default assumption with cost / scope impact. Resolving these is the highest-leverage path to refining the proposal — every answered Q-NNN may flip an open assumption from Assumed to Confirmed and reduce contingency.

| ID | Question | Default assumed | What an answer changes |
| --- | --- | --- | --- |
| Q-001 | P1 | TECH-ME | Confirm full list of BMS-monitored systems for this hotel. A |
| Q-005 | P1 | OWNER | Are guestroom-level HVAC controls (FCU per guestroom) in BMS |
| Q-007 | P1 | PROJECT | What is the required completion date / project duration? |
| Q-018 | P1 | PROJECT | The cover letter says “Rehabilitation” but the technical dra |
| Q-012 | P2 | TECH-IT | Is integration with FDAS, PMS, CCTV, or ACS required in this |
| Q-013 | P2 | OWNER | Confirm acceptable BMS brand list. Default: Siemens (Desigo |
| Q-014 | P2 | COMMERCIAL | Confirm payment terms, retention %, taxes, currency. |
| Q-015 | P2 | OWNER | Operator training duration and number of attendees. |
| Q-016 | P3 | OWNER | Is a 1-year preventive-maintenance contract requested with t |
| Q-002 | P2 | TECH-EE | EE Plan was provided as a Construction Bulletin set (raster) |
| Q-003 | P2 | TECH-ME | Provide architectural floor plans (corridors, ceiling voids, |
| Q-004 | P3 | TECH-EE | Confirm panel-board IDs and circuit assignments for the 25 d |
| Q-006 | P3 | TECH-IT | Confirm whether the BMS uplink lands on a dedicated VLAN on |
| Q-008 | P2 | TECH-ME | Per-guestroom FCU count per floor — confirm number of guestr |
| Q-009 | P3 | TECH-ME | Smoke control / kitchen exhaust interlocks — in BMS scope? |
| Q-010 | P3 | OWNER | Energy-savings algorithms required (chiller plant sequencing |
| Q-011 | P3 | OWNER | Number of BMS administrator (vs. operator) seats; remote-acc |
| Q-017 | P3 | COMMERCIAL | Confirm warranty period. |
| Q-019 | P3 | TECH-EE | Power-meter scope: confirm number and class (main vs. sub-fe |
| Q-020 | P3 | TECH-ME | Confirm number of BTU meters and chiller-side BACnet integra |

## 2. Verification action items (against drawings, on site, with vendors)

### Cable lengths — fallback rows to verify

Cables tagged legacy_fallback, typical_range:*, or fallback_a001 use agent-reasoned typical-range estimates rather than direct drawing measurements. These are the audit-XLSX rows the team should prioritize when the next set of drawings lands or when site walkthroughs become possible.

| Method tag | Count | Sample row ID |
| --- | --- | --- |
| typical_range:guestroom_zone_field | 180 | C0052 |
| typical_range:plant_room_same_room | 35 | C0019 |
| typical_range:same_floor_corridor_field | 26 | C0001 |
| typical_range:roofdeck_same_area | 15 | C0032 |
| typical_range:boh_corridor_field | 10 | C0007 |
| unknown | 3 | T0259 |
| typical_range | 1 | T0262 |

Open 13-A3-cable-schedule-AUDIT.xlsx to filter and prioritize.

### Other verification items

- Equipment counts — verify against mechanical floor plans where the agent inferred quantities (see open assumptions where Status: Open and category contains ‘count’).

- Panel locations — confirm against architectural drawings and walk the building if accessible.

- Drawing scale calibrations — if any A-NNN entries record drawing-scale calibration assumptions (e.g., grid-bay calibration), spot-check against a second known dimension before the proposal goes out.

- Vendor specifications — for every Equipment Supplier C/O cable / interface, confirm that the supplier’s panel architecture matches the assumed BMS-side interface (HLI vs. hardwired DI/DO).

## 3. Cost-reduction opportunities

### RFQ packages — competitive bidding

### Other cost levers

- Cable specifications — confirm with the customer whether the assumed jacket rating (e.g., FRLS) is mandated or whether a less-specified cable is acceptable in non-occupied spaces. Material cost difference can be 10–20% on cabling.

- Spare-conductor strategy — current strategy provides 15–25% spares per I/O class. If the customer is willing to accept lower spare margins (commit to the I/O list as-final), cable size drops and material cost reduces 5–10%.

- Make/model consolidation — RFQ packages currently call for spec-level equivalent items. If the customer accepts a single-vendor list (one controller brand, one valve brand), the team can negotiate volume discounts. Document any such consolidation in a new Q-NNN.

- Owner-furnished items — review C1 contractor/owner matrix; items currently assigned to BMS scope that the owner could supply directly (e.g., off-the-shelf workstations, network switches if customer has IT preferences) reduce BMS material markup.

## 4. Risks and decisions to revisit

### Risk register highlights

Open risks from D3-risk-register.md worth re-evaluating before issue:

- R-1 — Q-005 / Q-008 returns “every guestroom in scope” → +20–30% scope | Medium | High

- R-2 — Q-018 returns “actually rehab” → demolition + cutover scope | Low | High

- R-3 — Q-013 returns customer-specific brand list outside Siemens / Dell defaults | Medium | Low

- R-4 — Architectural drawings arrive at shop-stage with longer cable runs | Medium | Medium

- R-5 — EE-supplied panel feeds delayed (Q-004) | Low | Medium

- R-6 — Customer LAN integration delayed (Q-006) | Low | Low

## 5. Open assumptions to refine

0 assumptions in ‘Open’ status (out of 0 total). Each one is something the proposal currently treats as a known quantity but isn’t actually confirmed. The team should pair each open assumption with the corresponding Q-NNN and chase the customer’s answer.

## 6. Process improvements queued

Items the methodology audit and A/B regression runs flagged for the next playbook pass. These don’t block this proposal but will improve the next one:

- Conduit ratio — currently 30% of total cable length unless overridden. Project-tuned override available via B4-site-factors.yaml (see Op#11).

- Commercial rates — overhead 20% / contingency 7.5% / VAT 12% are defaults. Project-tuned override via 06-commercial-rates.yaml based on risk-register score.

- Cable specs — currently project-blind. Consider authoring A3-cable-spec-rules.yaml per _playbook/sub-routines/build-cable-schedule.md for explicit jurisdiction / brand reasoning.

- MS/TP trunk topology — formula-based fallback; ideally derived from actual A4 panel locations.

## 7. Defensibility check — what’s already strong

Reassurance for the team — items the agent already handled to a defensible standard:

- Every BOQ line traces to a working doc; every working doc cites sources

- Drawing-availability triage committed in writing in 03-doc-inventory.md (per Op#10)

- All assumptions are documented with rationale + impact-if-wrong

- 13-file deliverables package ready for issue with no missing artifacts

- Audit XLSX layer (per Principle F) makes verification work tractable

Generated by _playbook/tools/generate-internal-notes.py. Re-run after any update to the project’s working docs to refresh.