## Summary
A1 — Consolidated I/O List Summary
Project | Kingsford Hotel Bacolod — BMS
Total I/O rows | 753
By type
DI | 369
AI | 170
HLI | 102
AO | 68
Network | 29
DO | 15
By C/O
Equipment Supplier | 462
BMS Contractor | 232
ME Contractor | 59
By system
ventilation | 373
chilled_water | 135
common_area | 64
hot_water | 45
steam | 42
condenser_water | 40
casino_mvac | 38
power_metering | 11
btu_metering | 5
By panel
BMS-PNL-RD-MECH | 204
BMS-PNL-LG-CHILLER | 143
BMS-PNL-2F-CASINO | 91
BMS-PNL-3F | 76
BMS-PNL-GF | 68
BMS-PNL-LG-PLUMB | 67
BMS-PNL-B1 | 64
BMS-PNL-RD-CT | 40

## All IO Points
ID | System | Equipment Class | Equipment Instance | Location | Point Description | Type | Field Device | C/O | DoO Ref | Panel | Source | Notes
P0001 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Compressor on/off status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0002 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Compressor H/O/A status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0003 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Compressor trip alarm | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0004 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Motor load current | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0005 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Motor consumption (kW) | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0006 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Motor winding temperature | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0007 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Oil sump pressure | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0008 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Oil sump temperature | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0009 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Oil pump on/off status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0010 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Oil pump trip | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0011 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Evaporator approach delta-T | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0012 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Evaporator approach delta-P | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0013 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Evaporator refrigerant pressure | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0014 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Evaporator refrigerant temperature | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0015 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Condenser refrigerant pressure | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0016 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Condenser refrigerant temperature | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0017 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Condenser approach delta-T | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0018 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Condenser approach delta-P | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0019 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Entering CHW temperature | AI | Temperature Sensor (immersion) | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0020 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Leaving CHW temperature | AI | Temperature Sensor (immersion) | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0021 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Entering condenser water temperature | AI | Temperature Sensor (immersion) | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0022 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Leaving condenser water temperature | AI | Temperature Sensor (immersion) | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0023 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Chiller native BACnet/IP gateway | Network | BACnet/IP | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0024 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | CHW Supply isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0025 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | CHW Return isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0026 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Condenser Water Supply isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0027 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Condenser Water Return isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0028 | chilled_water | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Mechanical Room | Start permissive | DO | Relay output | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0029 | chilled_water | Primary CHW Pump | PCHWP-1 | 2nd Level Mechanical Room | Pump motor on/off status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0030 | chilled_water | Primary CHW Pump | PCHWP-1 | 2nd Level Mechanical Room | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0031 | chilled_water | Primary CHW Pump | PCHWP-1 | 2nd Level Mechanical Room | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0032 | chilled_water | Primary CHW Pump | PCHWP-1 | 2nd Level Mechanical Room | VFD speed feedback | AI | VFD analog output / 4-20 mA | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0033 | chilled_water | Primary CHW Pump | PCHWP-1 | 2nd Level Mechanical Room | VFD speed command | AO | 0-10V / 4-20 mA out | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0034 | chilled_water | Primary CHW Pump | PCHWP-1 | 2nd Level Mechanical Room | CHW supply pressure (per pump) | AI | Pressure Transmitter | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0035 | chilled_water | Primary CHW Pump | PCHWP-1 | 2nd Level Mechanical Room | VFD network HLI (run hours, fault, kWh) | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0036 | chilled_water | Primary CHW Pump | PCHWP-1 | 2nd Level Mechanical Room | Pump start command | DO | Relay output | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0037 | chilled_water | Condenser Water Pump | CWP-1 | 2nd Level Mechanical Room | Pump motor on/off status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0038 | chilled_water | Condenser Water Pump | CWP-1 | 2nd Level Mechanical Room | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0039 | chilled_water | Condenser Water Pump | CWP-1 | 2nd Level Mechanical Room | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0040 | chilled_water | Condenser Water Pump | CWP-1 | 2nd Level Mechanical Room | Pump start command | DO | Relay output | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0041 | chilled_water | Condenser Water Pump | CWP-1 | 2nd Level Mechanical Room | Pump VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0042 | chilled_water | Condenser Water Pump | CWP-1 | 2nd Level Mechanical Room | VFD network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0043 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Compressor on/off status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0044 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Compressor H/O/A status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0045 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Compressor trip alarm | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0046 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Motor load current | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0047 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Motor consumption (kW) | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0048 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Motor winding temperature | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0049 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Oil sump pressure | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0050 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Oil sump temperature | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0051 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Oil pump on/off status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0052 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Oil pump trip | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0053 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Evaporator approach delta-T | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0054 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Evaporator approach delta-P | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0055 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Evaporator refrigerant pressure | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0056 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Evaporator refrigerant temperature | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0057 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Condenser refrigerant pressure | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0058 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Condenser refrigerant temperature | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0059 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Condenser approach delta-T | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0060 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Condenser approach delta-P | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0061 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Entering CHW temperature | AI | Temperature Sensor (immersion) | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0062 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Leaving CHW temperature | AI | Temperature Sensor (immersion) | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0063 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Entering condenser water temperature | AI | Temperature Sensor (immersion) | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0064 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Leaving condenser water temperature | AI | Temperature Sensor (immersion) | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0065 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Chiller native BACnet/IP gateway | Network | BACnet/IP | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0066 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | CHW Supply isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0067 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | CHW Return isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0068 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Condenser Water Supply isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0069 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Condenser Water Return isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0070 | chilled_water | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Mechanical Room | Start permissive | DO | Relay output | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0071 | chilled_water | Primary CHW Pump | PCHWP-2 | 2nd Level Mechanical Room | Pump motor on/off status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0072 | chilled_water | Primary CHW Pump | PCHWP-2 | 2nd Level Mechanical Room | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0073 | chilled_water | Primary CHW Pump | PCHWP-2 | 2nd Level Mechanical Room | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0074 | chilled_water | Primary CHW Pump | PCHWP-2 | 2nd Level Mechanical Room | VFD speed feedback | AI | VFD analog output / 4-20 mA | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0075 | chilled_water | Primary CHW Pump | PCHWP-2 | 2nd Level Mechanical Room | VFD speed command | AO | 0-10V / 4-20 mA out | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0076 | chilled_water | Primary CHW Pump | PCHWP-2 | 2nd Level Mechanical Room | CHW supply pressure (per pump) | AI | Pressure Transmitter | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0077 | chilled_water | Primary CHW Pump | PCHWP-2 | 2nd Level Mechanical Room | VFD network HLI (run hours, fault, kWh) | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0078 | chilled_water | Primary CHW Pump | PCHWP-2 | 2nd Level Mechanical Room | Pump start command | DO | Relay output | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0079 | chilled_water | Condenser Water Pump | CWP-2 | 2nd Level Mechanical Room | Pump motor on/off status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0080 | chilled_water | Condenser Water Pump | CWP-2 | 2nd Level Mechanical Room | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0081 | chilled_water | Condenser Water Pump | CWP-2 | 2nd Level Mechanical Room | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0082 | chilled_water | Condenser Water Pump | CWP-2 | 2nd Level Mechanical Room | Pump start command | DO | Relay output | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0083 | chilled_water | Condenser Water Pump | CWP-2 | 2nd Level Mechanical Room | Pump VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0084 | chilled_water | Condenser Water Pump | CWP-2 | 2nd Level Mechanical Room | VFD network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0085 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Compressor on/off status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0086 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Compressor H/O/A status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0087 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Compressor trip alarm | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0088 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Motor load current | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0089 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Motor consumption (kW) | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0090 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Motor winding temperature | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0091 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Oil sump pressure | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0092 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Oil sump temperature | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0093 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Oil pump on/off status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0094 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Oil pump trip | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0095 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Evaporator approach delta-T | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0096 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Evaporator approach delta-P | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0097 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Evaporator refrigerant pressure | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0098 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Evaporator refrigerant temperature | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0099 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Condenser refrigerant pressure | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0100 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Condenser refrigerant temperature | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0101 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Condenser approach delta-T | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0102 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Condenser approach delta-P | HLI | — | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0103 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Entering CHW temperature | AI | Temperature Sensor (immersion) | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0104 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Leaving CHW temperature | AI | Temperature Sensor (immersion) | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0105 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Entering condenser water temperature | AI | Temperature Sensor (immersion) | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0106 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Leaving condenser water temperature | AI | Temperature Sensor (immersion) | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0107 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Chiller native BACnet/IP gateway | Network | BACnet/IP | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0108 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | CHW Supply isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0109 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | CHW Return isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0110 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Condenser Water Supply isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0111 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Condenser Water Return isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0112 | chilled_water | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Mechanical Room | Start permissive | DO | Relay output | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0113 | chilled_water | Primary CHW Pump | PCHWP-3 | 2nd Level Mechanical Room | Pump motor on/off status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0114 | chilled_water | Primary CHW Pump | PCHWP-3 | 2nd Level Mechanical Room | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0115 | chilled_water | Primary CHW Pump | PCHWP-3 | 2nd Level Mechanical Room | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0116 | chilled_water | Primary CHW Pump | PCHWP-3 | 2nd Level Mechanical Room | VFD speed feedback | AI | VFD analog output / 4-20 mA | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0117 | chilled_water | Primary CHW Pump | PCHWP-3 | 2nd Level Mechanical Room | VFD speed command | AO | 0-10V / 4-20 mA out | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0118 | chilled_water | Primary CHW Pump | PCHWP-3 | 2nd Level Mechanical Room | CHW supply pressure (per pump) | AI | Pressure Transmitter | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0119 | chilled_water | Primary CHW Pump | PCHWP-3 | 2nd Level Mechanical Room | VFD network HLI (run hours, fault, kWh) | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0120 | chilled_water | Primary CHW Pump | PCHWP-3 | 2nd Level Mechanical Room | Pump start command | DO | Relay output | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0121 | chilled_water | Condenser Water Pump | CWP-3 | 2nd Level Mechanical Room | Pump motor on/off status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0122 | chilled_water | Condenser Water Pump | CWP-3 | 2nd Level Mechanical Room | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0123 | chilled_water | Condenser Water Pump | CWP-3 | 2nd Level Mechanical Room | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0124 | chilled_water | Condenser Water Pump | CWP-3 | 2nd Level Mechanical Room | Pump start command | DO | Relay output | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0125 | chilled_water | Condenser Water Pump | CWP-3 | 2nd Level Mechanical Room | Pump VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0126 | chilled_water | Condenser Water Pump | CWP-3 | 2nd Level Mechanical Room | VFD network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0127 | chilled_water | CHW Supply Main Header | CHW-HDR-S | 2nd Level Mechanical Room | CHW supply header temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0128 | chilled_water | CHW Supply Main Header | CHW-HDR-S | 2nd Level Mechanical Room | CHW supply header pressure | AI | Pressure Transmitter | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0129 | chilled_water | CHW Return Main Header | CHW-HDR-R | 2nd Level Mechanical Room | CHW return header temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0130 | chilled_water | CHW Return Main Header | CHW-HDR-R | 2nd Level Mechanical Room | CHW return header pressure | AI | Pressure Transmitter | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0131 | chilled_water | CHW Bypass Header | CHW-BYPASS | 2nd Level Mechanical Room | CHW differential pressure | AI | Diff. Pressure Sensor | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0132 | chilled_water | CHW Bypass Header | CHW-BYPASS | 2nd Level Mechanical Room | CHW differential temperature | AI | Diff. Temp Sensor | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0133 | chilled_water | CHW Bypass Header | CHW-BYPASS | 2nd Level Mechanical Room | Bypass motorized valve command | AO | Electric Valve Actuator | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0134 | chilled_water | CHW Bypass Header | CHW-BYPASS | 2nd Level Mechanical Room | Bypass motorized valve feedback | AI | Position Feedback | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0135 | chilled_water | CHW Bypass Header | CHW-BYPASS | 2nd Level Mechanical Room | Bypass valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0136 | condenser_water | Cooling Tower | CT-1 | Roof Deck Mechanical | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0137 | condenser_water | Cooling Tower | CT-1 | Roof Deck Mechanical | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0138 | condenser_water | Cooling Tower | CT-1 | Roof Deck Mechanical | Fan start command | DO | Relay output | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0139 | condenser_water | Cooling Tower | CT-1 | Roof Deck Mechanical | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0140 | condenser_water | Cooling Tower | CT-1 | Roof Deck Mechanical | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0141 | condenser_water | Cooling Tower | CT-1 | Roof Deck Mechanical | Basin level low alarm | DI | Level Electrode | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0142 | condenser_water | Cooling Tower | CT-1 | Roof Deck Mechanical | Basin level high alarm | DI | Level Electrode | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0143 | condenser_water | Cooling Tower | CT-1 | Roof Deck Mechanical | Outside air temperature (local) | AI | OA Temperature Sensor | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0144 | condenser_water | Cooling Tower | CT-1 | Roof Deck Mechanical | Outside air humidity (local) | AI | OA Humidity Sensor | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0145 | condenser_water | Cooling Tower | CT-1 | Roof Deck Mechanical | CT supply isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0146 | condenser_water | Cooling Tower | CT-1 | Roof Deck Mechanical | CT return isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0147 | condenser_water | Cooling Tower | CT-1 | Roof Deck Mechanical | Motorized blowdown valve control | DO | Electric Valve Actuator | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0148 | condenser_water | Cooling Tower | CT-2 | Roof Deck Mechanical | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0149 | condenser_water | Cooling Tower | CT-2 | Roof Deck Mechanical | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0150 | condenser_water | Cooling Tower | CT-2 | Roof Deck Mechanical | Fan start command | DO | Relay output | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0151 | condenser_water | Cooling Tower | CT-2 | Roof Deck Mechanical | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0152 | condenser_water | Cooling Tower | CT-2 | Roof Deck Mechanical | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0153 | condenser_water | Cooling Tower | CT-2 | Roof Deck Mechanical | Basin level low alarm | DI | Level Electrode | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0154 | condenser_water | Cooling Tower | CT-2 | Roof Deck Mechanical | Basin level high alarm | DI | Level Electrode | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0155 | condenser_water | Cooling Tower | CT-2 | Roof Deck Mechanical | Outside air temperature (local) | AI | OA Temperature Sensor | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0156 | condenser_water | Cooling Tower | CT-2 | Roof Deck Mechanical | Outside air humidity (local) | AI | OA Humidity Sensor | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0157 | condenser_water | Cooling Tower | CT-2 | Roof Deck Mechanical | CT supply isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0158 | condenser_water | Cooling Tower | CT-2 | Roof Deck Mechanical | CT return isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0159 | condenser_water | Cooling Tower | CT-2 | Roof Deck Mechanical | Motorized blowdown valve control | DO | Electric Valve Actuator | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0160 | condenser_water | Cooling Tower | CT-3 | Roof Deck Mechanical | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0161 | condenser_water | Cooling Tower | CT-3 | Roof Deck Mechanical | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0162 | condenser_water | Cooling Tower | CT-3 | Roof Deck Mechanical | Fan start command | DO | Relay output | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0163 | condenser_water | Cooling Tower | CT-3 | Roof Deck Mechanical | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0164 | condenser_water | Cooling Tower | CT-3 | Roof Deck Mechanical | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0165 | condenser_water | Cooling Tower | CT-3 | Roof Deck Mechanical | Basin level low alarm | DI | Level Electrode | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0166 | condenser_water | Cooling Tower | CT-3 | Roof Deck Mechanical | Basin level high alarm | DI | Level Electrode | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0167 | condenser_water | Cooling Tower | CT-3 | Roof Deck Mechanical | Outside air temperature (local) | AI | OA Temperature Sensor | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0168 | condenser_water | Cooling Tower | CT-3 | Roof Deck Mechanical | Outside air humidity (local) | AI | OA Humidity Sensor | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0169 | condenser_water | Cooling Tower | CT-3 | Roof Deck Mechanical | CT supply isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0170 | condenser_water | Cooling Tower | CT-3 | Roof Deck Mechanical | CT return isolation valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0171 | condenser_water | Cooling Tower | CT-3 | Roof Deck Mechanical | Motorized blowdown valve control | DO | Electric Valve Actuator | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0172 | condenser_water | Cooling Tower (Common) | CT-COMMON | Roof Deck Mechanical | Condenser supply header temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0173 | condenser_water | Cooling Tower (Common) | CT-COMMON | Roof Deck Mechanical | Condenser return header temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0174 | condenser_water | Cooling Tower (Common) | CT-COMMON | Roof Deck Mechanical | Condenser water pH (corrosion) | AI | pH Sensor | ME Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0175 | condenser_water | Cooling Tower (Common) | CT-COMMON | Roof Deck Mechanical | Condenser water conductivity (scale) | AI | Conductivity Sensor | ME Contractor |  | BMS-PNL-RD-CT | BMS Points list (TUEC) + ME/PL Points list
P0176 | btu_metering | BTU Meter | BTU-1 | 2nd Level Mechanical Room | BTU meter (energy reading) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0177 | btu_metering | BTU Meter | BTU-2 | 2nd Level Mechanical Room | BTU meter (energy reading) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0178 | btu_metering | BTU Meter | BTU-3 | 2nd Level Mechanical Room | BTU meter (energy reading) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0179 | btu_metering | BTU Meter | BTU-4 | 2nd Level Mechanical Room | BTU meter (energy reading) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0180 | btu_metering | BTU Meter | BTU-5 | 2nd Level Mechanical Room | BTU meter (energy reading) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0181 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0182 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Outside SA flow | AI | Air Flow Station | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0183 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Outside SA humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0184 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0185 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | OA motorized damper command | AO | Damper Actuator | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0186 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Recovery wheel motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0187 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Recovery wheel trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0188 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Supply fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0189 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Supply fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0190 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Supply fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0191 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Supply fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0192 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Supply fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0193 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0194 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Mixed air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0195 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | CHWS / cooling-coil valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0196 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | CHWS / cooling-coil valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0197 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Indoor supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0198 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Indoor exhaust air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0199 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Indoor exhaust air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0200 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Exhaust fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0201 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Exhaust fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0202 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Exhaust fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0203 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Exhaust fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0204 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | Exhaust fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0205 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | DOAS network HLI (VFDs, kWh) | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0206 | ventilation | DOAS Unit | DOAS-RD1 | Roof Deck Mechanical | DOAS network drop | Network | BACnet/IP | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0207 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0208 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Outside SA flow | AI | Air Flow Station | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0209 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Outside SA humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0210 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0211 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | OA motorized damper command | AO | Damper Actuator | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0212 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Recovery wheel motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0213 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Recovery wheel trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0214 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Supply fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0215 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Supply fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0216 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Supply fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0217 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Supply fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0218 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Supply fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0219 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0220 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Mixed air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0221 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | CHWS / cooling-coil valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0222 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | CHWS / cooling-coil valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0223 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Indoor supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0224 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Indoor exhaust air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0225 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Indoor exhaust air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0226 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Exhaust fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0227 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Exhaust fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0228 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Exhaust fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0229 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Exhaust fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0230 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | Exhaust fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0231 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | DOAS network HLI (VFDs, kWh) | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0232 | ventilation | DOAS Unit | DOAS-RD2 | Roof Deck Mechanical | DOAS network drop | Network | BACnet/IP | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0233 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0234 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Outside SA flow | AI | Air Flow Station | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0235 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Outside SA humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0236 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0237 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | OA motorized damper command | AO | Damper Actuator | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0238 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Recovery wheel motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0239 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Recovery wheel trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0240 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Supply fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0241 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Supply fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0242 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Supply fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0243 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Supply fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0244 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Supply fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0245 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0246 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Mixed air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0247 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | CHWS / cooling-coil valve status | DI | Auxiliary Contact | ME Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0248 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | CHWS / cooling-coil valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0249 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Indoor supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0250 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Indoor exhaust air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0251 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Indoor exhaust air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0252 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Exhaust fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0253 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Exhaust fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0254 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Exhaust fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0255 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Exhaust fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0256 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | Exhaust fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0257 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | DOAS network HLI (VFDs, kWh) | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0258 | ventilation | DOAS Unit | DOAS-2F-CASINO | 2nd Floor Casino MVAC Room | DOAS network drop | Network | BACnet/IP | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0259 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0260 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | Outside SA flow | AI | Air Flow Station | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0261 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0262 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0263 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | CHWS / cooling-coil valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0264 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0265 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0266 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0267 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0268 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0269 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | Indoor supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0270 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0271 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | Mixed air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0272 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | Filter differential pressure (high) | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0273 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | PAHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0274 | ventilation | Precooled Air Handling Unit | PAHU-01 | Roof Deck Mechanical | PAHU network drop | Network | BACnet/IP | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0275 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0276 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | Outside SA flow | AI | Air Flow Station | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0277 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0278 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0279 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | CHWS / cooling-coil valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0280 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0281 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0282 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0283 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0284 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0285 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | Indoor supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0286 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0287 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | Mixed air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0288 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | Filter differential pressure (high) | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0289 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | PAHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0290 | ventilation | Precooled Air Handling Unit | PAHU-02 | Roof Deck Mechanical | PAHU network drop | Network | BACnet/IP | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0291 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0292 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | Outside SA flow | AI | Air Flow Station | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0293 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0294 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0295 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | CHWS / cooling-coil valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0296 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0297 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0298 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0299 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0300 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0301 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | Indoor supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0302 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0303 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | Mixed air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0304 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | Filter differential pressure (high) | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0305 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | PAHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0306 | ventilation | Precooled Air Handling Unit | PAHU-03 | Roof Deck Mechanical | PAHU network drop | Network | BACnet/IP | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0307 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0308 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | Outside SA flow | AI | Air Flow Station | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0309 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0310 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0311 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | CHWS / cooling-coil valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0312 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0313 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0314 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0315 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0316 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0317 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | Indoor supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0318 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0319 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | Mixed air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0320 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | Filter differential pressure (high) | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0321 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | PAHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0322 | ventilation | Precooled Air Handling Unit | PAHU-04 | Roof Deck Mechanical | PAHU network drop | Network | BACnet/IP | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0323 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0324 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | Outside SA flow | AI | Air Flow Station | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0325 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0326 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0327 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | CHWS / cooling-coil valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0328 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0329 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0330 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0331 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0332 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0333 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | Indoor supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0334 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0335 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | Mixed air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0336 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | Filter differential pressure (high) | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0337 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | PAHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0338 | ventilation | Precooled Air Handling Unit | PAHU-05 | Roof Deck Mechanical | PAHU network drop | Network | BACnet/IP | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0339 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0340 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | Outside SA flow | AI | Air Flow Station | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0341 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0342 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0343 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | CHWS / cooling-coil valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0344 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0345 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0346 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0347 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0348 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0349 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | Indoor supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0350 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0351 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | Mixed air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0352 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | Filter differential pressure (high) | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0353 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | PAHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0354 | ventilation | Precooled Air Handling Unit | PAHU-06 | Roof Deck Mechanical | PAHU network drop | Network | BACnet/IP | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0355 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0356 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | Outside SA flow | AI | Air Flow Station | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0357 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0358 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0359 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | CHWS / cooling-coil valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0360 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0361 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0362 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0363 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0364 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0365 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | Indoor supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0366 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0367 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | Mixed air humidity | AI | Duct RH Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0368 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | Filter differential pressure (high) | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0369 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | PAHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0370 | ventilation | Precooled Air Handling Unit | PAHU-07 | Roof Deck Mechanical | PAHU network drop | Network | BACnet/IP | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0371 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Return air motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0372 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Return air motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0373 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Return air CO2 (DCV) | AI | CO2 Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0374 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Return air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0375 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0376 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0377 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | CHWS valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0378 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0379 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0380 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0381 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0382 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0383 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0384 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0385 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Filter differential pressure | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0386 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | AHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0387 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Floor Casino MVAC Room | Casino return-air CO sensor | AI | CO Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0388 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Return air motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0389 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Return air motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0390 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Return air CO2 (DCV) | AI | CO2 Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0391 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Return air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0392 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0393 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0394 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | CHWS valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0395 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0396 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0397 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0398 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0399 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0400 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0401 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0402 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Filter differential pressure | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0403 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | AHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0404 | casino_mvac | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Floor Casino MVAC Room | Casino return-air CO sensor | AI | CO Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0405 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | Return air motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0406 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | Return air motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0407 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | Return air CO2 (DCV) | AI | CO2 Sensor | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0408 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | Return air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0409 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0410 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | Supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0411 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | CHWS valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0412 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0413 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0414 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0415 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0416 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0417 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0418 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0419 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | Filter differential pressure | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0420 | common_area | AHU (Chilled-Water-Served) | AHU-GF-1 | Ground Floor BOH | AHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0421 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | Return air motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0422 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | Return air motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0423 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | Return air CO2 (DCV) | AI | CO2 Sensor | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0424 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | Return air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0425 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0426 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | Supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0427 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | CHWS valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0428 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0429 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0430 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0431 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0432 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0433 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0434 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0435 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | Filter differential pressure | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0436 | common_area | AHU (Chilled-Water-Served) | AHU-GFM-1 | Ground Floor Mezzanine BOH | AHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0437 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | Return air motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0438 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | Return air motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0439 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | Return air CO2 (DCV) | AI | CO2 Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0440 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | Return air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0441 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0442 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | Supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0443 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | CHWS valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0444 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0445 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0446 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0447 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0448 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0449 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0450 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0451 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | Filter differential pressure | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0452 | common_area | AHU (Chilled-Water-Served) | AHU-2F-1 | 2nd Floor BOH | AHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0453 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | Return air motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0454 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | Return air motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0455 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | Return air CO2 (DCV) | AI | CO2 Sensor | BMS Contractor |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0456 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | Return air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0457 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | Mixed air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0458 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | Supply air temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0459 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | CHWS valve command | AO | Electric Valve Actuator | ME Contractor |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0460 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0461 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0462 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | Fan VFD speed command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0463 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | Fan VFD speed feedback | AI | VFD analog output | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0464 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | OA motorized damper status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0465 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | OA motorized damper command | AO | Damper Actuator | ME Contractor |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0466 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | Outside SA temperature | AI | Duct Temp Sensor | BMS Contractor |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0467 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | Filter differential pressure | DI | Diff. Pressure Switch | BMS Contractor |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0468 | common_area | AHU (Chilled-Water-Served) | AHU-B1-1 | Basement 1 BOH | AHU network HLI | HLI | BACnet/Modbus card | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0469 | casino_mvac | Ozone Generator (UV-light or Corona) | ION-2F-1 | 2nd Floor Casino | Ionizer run status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0470 | casino_mvac | Ozone Generator (UV-light or Corona) | ION-2F-1 | 2nd Floor Casino | Ionizer fault status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0471 | casino_mvac | Ozone Generator (UV-light or Corona) | ION-2F-2 | 2nd Floor Casino | Ionizer run status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0472 | casino_mvac | Ozone Generator (UV-light or Corona) | ION-2F-2 | 2nd Floor Casino | Ionizer fault status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0473 | ventilation | Exhaust Fan (Toilet) | TEF-2.1 | 2nd Floor BOH | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0474 | ventilation | Exhaust Fan (Toilet) | TEF-2.1 | 2nd Floor BOH | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0475 | ventilation | Exhaust Fan (Toilet) | TEF-2.1 | 2nd Floor BOH | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0476 | ventilation | Exhaust Fan (Toilet) | TEF-2.3 | 2nd Floor BOH | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0477 | ventilation | Exhaust Fan (Toilet) | TEF-2.3 | 2nd Floor BOH | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0478 | ventilation | Exhaust Fan (Toilet) | TEF-2.3 | 2nd Floor BOH | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0479 | ventilation | Exhaust Fan (Toilet) | TEF-2B.3 | 2nd Floor BOH | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0480 | ventilation | Exhaust Fan (Toilet) | TEF-2B.3 | 2nd Floor BOH | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0481 | ventilation | Exhaust Fan (Toilet) | TEF-2B.3 | 2nd Floor BOH | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0482 | ventilation | Exhaust Fan (Toilet) | TEF-GS.1 | Ground Floor | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0483 | ventilation | Exhaust Fan (Toilet) | TEF-GS.1 | Ground Floor | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0484 | ventilation | Exhaust Fan (Toilet) | TEF-GS.1 | Ground Floor | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0485 | ventilation | Exhaust Fan (Toilet) | TEF-GS.2 | Ground Floor | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0486 | ventilation | Exhaust Fan (Toilet) | TEF-GS.2 | Ground Floor | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0487 | ventilation | Exhaust Fan (Toilet) | TEF-GS.2 | Ground Floor | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0488 | ventilation | Exhaust Fan (Toilet) | TEF-1.1 | Ground Floor Lobby | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0489 | ventilation | Exhaust Fan (Toilet) | TEF-1.1 | Ground Floor Lobby | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0490 | ventilation | Exhaust Fan (Toilet) | TEF-1.1 | Ground Floor Lobby | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0491 | ventilation | Exhaust Fan (Toilet) | TEF-1.2 | Ground Floor Lobby | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0492 | ventilation | Exhaust Fan (Toilet) | TEF-1.2 | Ground Floor Lobby | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0493 | ventilation | Exhaust Fan (Toilet) | TEF-1.2 | Ground Floor Lobby | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0494 | ventilation | Exhaust Fan (Toilet) | TEF-1.3 | Ground Floor Lobby | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0495 | ventilation | Exhaust Fan (Toilet) | TEF-1.3 | Ground Floor Lobby | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0496 | ventilation | Exhaust Fan (Toilet) | TEF-1.3 | Ground Floor Lobby | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0497 | ventilation | Exhaust Fan (Toilet) | TEF-1.4 | Ground Floor Lobby | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0498 | ventilation | Exhaust Fan (Toilet) | TEF-1.4 | Ground Floor Lobby | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0499 | ventilation | Exhaust Fan (Toilet) | TEF-1.4 | Ground Floor Lobby | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0500 | ventilation | Exhaust Fan (Toilet) | TEF-3A.1 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0501 | ventilation | Exhaust Fan (Toilet) | TEF-3A.1 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0502 | ventilation | Exhaust Fan (Toilet) | TEF-3A.1 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0503 | ventilation | Exhaust Fan (Toilet) | TEF-3A.2 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0504 | ventilation | Exhaust Fan (Toilet) | TEF-3A.2 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0505 | ventilation | Exhaust Fan (Toilet) | TEF-3A.2 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0506 | ventilation | Exhaust Fan (Toilet) | TEF-3B | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0507 | ventilation | Exhaust Fan (Toilet) | TEF-3B | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0508 | ventilation | Exhaust Fan (Toilet) | TEF-3B | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0509 | ventilation | Exhaust Fan (Toilet) | TEF-3C.1 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0510 | ventilation | Exhaust Fan (Toilet) | TEF-3C.1 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0511 | ventilation | Exhaust Fan (Toilet) | TEF-3C.1 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0512 | ventilation | Exhaust Fan (Toilet) | TEF-3C.2 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0513 | ventilation | Exhaust Fan (Toilet) | TEF-3C.2 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0514 | ventilation | Exhaust Fan (Toilet) | TEF-3C.2 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0515 | ventilation | Exhaust Fan (Toilet) | TEF-3D.1 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0516 | ventilation | Exhaust Fan (Toilet) | TEF-3D.1 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0517 | ventilation | Exhaust Fan (Toilet) | TEF-3D.1 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0518 | ventilation | Exhaust Fan (Toilet) | TEF-3D.2 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0519 | ventilation | Exhaust Fan (Toilet) | TEF-3D.2 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0520 | ventilation | Exhaust Fan (Toilet) | TEF-3D.2 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0521 | ventilation | Exhaust Fan (Toilet) | TEF-3D.3 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0522 | ventilation | Exhaust Fan (Toilet) | TEF-3D.3 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0523 | ventilation | Exhaust Fan (Toilet) | TEF-3D.3 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0524 | ventilation | Exhaust Fan (Toilet) | TEF-3D.4 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0525 | ventilation | Exhaust Fan (Toilet) | TEF-3D.4 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0526 | ventilation | Exhaust Fan (Toilet) | TEF-3D.4 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0527 | ventilation | Exhaust Fan (Toilet) | TEF-3D.5 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0528 | ventilation | Exhaust Fan (Toilet) | TEF-3D.5 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0529 | ventilation | Exhaust Fan (Toilet) | TEF-3D.5 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0530 | ventilation | Exhaust Fan (Toilet) | TEF-3D.6 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0531 | ventilation | Exhaust Fan (Toilet) | TEF-3D.6 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0532 | ventilation | Exhaust Fan (Toilet) | TEF-3D.6 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0533 | ventilation | Exhaust Fan (Toilet) | TEF-3D.7 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0534 | ventilation | Exhaust Fan (Toilet) | TEF-3D.7 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0535 | ventilation | Exhaust Fan (Toilet) | TEF-3D.7 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0536 | ventilation | Exhaust Fan (Toilet) | TEF-3D.8 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0537 | ventilation | Exhaust Fan (Toilet) | TEF-3D.8 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0538 | ventilation | Exhaust Fan (Toilet) | TEF-3D.8 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0539 | ventilation | Exhaust Fan (Toilet) | TEF-3D.9 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0540 | ventilation | Exhaust Fan (Toilet) | TEF-3D.9 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0541 | ventilation | Exhaust Fan (Toilet) | TEF-3D.9 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0542 | ventilation | Exhaust Fan (Toilet) | TEF-3D.10 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0543 | ventilation | Exhaust Fan (Toilet) | TEF-3D.10 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0544 | ventilation | Exhaust Fan (Toilet) | TEF-3D.10 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0545 | ventilation | Exhaust Fan (Toilet) | TEF-3D.11 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0546 | ventilation | Exhaust Fan (Toilet) | TEF-3D.11 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0547 | ventilation | Exhaust Fan (Toilet) | TEF-3D.11 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0548 | ventilation | Exhaust Fan (Toilet) | TEF-3D.12 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0549 | ventilation | Exhaust Fan (Toilet) | TEF-3D.12 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0550 | ventilation | Exhaust Fan (Toilet) | TEF-3D.12 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0551 | ventilation | Exhaust Fan (Toilet) | TEF-3D.13 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0552 | ventilation | Exhaust Fan (Toilet) | TEF-3D.13 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0553 | ventilation | Exhaust Fan (Toilet) | TEF-3D.13 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0554 | ventilation | Exhaust Fan (Toilet) | TEF-3D.14 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0555 | ventilation | Exhaust Fan (Toilet) | TEF-3D.14 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0556 | ventilation | Exhaust Fan (Toilet) | TEF-3D.14 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0557 | ventilation | Exhaust Fan (Toilet) | TEF-3D.15 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0558 | ventilation | Exhaust Fan (Toilet) | TEF-3D.15 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0559 | ventilation | Exhaust Fan (Toilet) | TEF-3D.15 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0560 | ventilation | Exhaust Fan (Toilet) | TEF-3D.16 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0561 | ventilation | Exhaust Fan (Toilet) | TEF-3D.16 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0562 | ventilation | Exhaust Fan (Toilet) | TEF-3D.16 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0563 | ventilation | Exhaust Fan (Toilet) | TEF-3D.17 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0564 | ventilation | Exhaust Fan (Toilet) | TEF-3D.17 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0565 | ventilation | Exhaust Fan (Toilet) | TEF-3D.17 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0566 | ventilation | Exhaust Fan (Toilet) | TEF-3D.18 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0567 | ventilation | Exhaust Fan (Toilet) | TEF-3D.18 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0568 | ventilation | Exhaust Fan (Toilet) | TEF-3D.18 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0569 | ventilation | Exhaust Fan (Toilet) | TEF-3D.19 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0570 | ventilation | Exhaust Fan (Toilet) | TEF-3D.19 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0571 | ventilation | Exhaust Fan (Toilet) | TEF-3D.19 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0572 | ventilation | Exhaust Fan (Toilet) | TEF-3D.20 | 3rd Floor Amenity | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0573 | ventilation | Exhaust Fan (Toilet) | TEF-3D.20 | 3rd Floor Amenity | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0574 | ventilation | Exhaust Fan (Toilet) | TEF-3D.20 | 3rd Floor Amenity | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0575 | ventilation | Exhaust Fan (Toilet) | TEF-B.1 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0576 | ventilation | Exhaust Fan (Toilet) | TEF-B.1 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0577 | ventilation | Exhaust Fan (Toilet) | TEF-B.1 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0578 | ventilation | Exhaust Fan (Toilet) | TEF-B.2 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0579 | ventilation | Exhaust Fan (Toilet) | TEF-B.2 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0580 | ventilation | Exhaust Fan (Toilet) | TEF-B.2 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0581 | ventilation | Exhaust Fan (Toilet) | TEF-B.3 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0582 | ventilation | Exhaust Fan (Toilet) | TEF-B.3 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0583 | ventilation | Exhaust Fan (Toilet) | TEF-B.3 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0584 | ventilation | Exhaust Fan (Toilet) | TEF-B.4 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0585 | ventilation | Exhaust Fan (Toilet) | TEF-B.4 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0586 | ventilation | Exhaust Fan (Toilet) | TEF-B.4 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0587 | ventilation | Exhaust Fan (Toilet) | TEF-B.5 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0588 | ventilation | Exhaust Fan (Toilet) | TEF-B.5 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0589 | ventilation | Exhaust Fan (Toilet) | TEF-B.5 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0590 | ventilation | Exhaust Fan (Toilet) | TEF-B.6 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0591 | ventilation | Exhaust Fan (Toilet) | TEF-B.6 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0592 | ventilation | Exhaust Fan (Toilet) | TEF-B.6 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0593 | ventilation | Exhaust Fan (Toilet) | TEF-B.7 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0594 | ventilation | Exhaust Fan (Toilet) | TEF-B.7 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0595 | ventilation | Exhaust Fan (Toilet) | TEF-B.7 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0596 | ventilation | Exhaust Fan (Toilet) | TEF-B.8 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0597 | ventilation | Exhaust Fan (Toilet) | TEF-B.8 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0598 | ventilation | Exhaust Fan (Toilet) | TEF-B.8 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0599 | ventilation | Exhaust Fan (Toilet) | TEF-B.9 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0600 | ventilation | Exhaust Fan (Toilet) | TEF-B.9 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0601 | ventilation | Exhaust Fan (Toilet) | TEF-B.9 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0602 | ventilation | Exhaust Fan (Toilet) | TEF-B.10 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0603 | ventilation | Exhaust Fan (Toilet) | TEF-B.10 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0604 | ventilation | Exhaust Fan (Toilet) | TEF-B.10 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0605 | ventilation | Exhaust Fan (Toilet) | TEF-B.11 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0606 | ventilation | Exhaust Fan (Toilet) | TEF-B.11 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0607 | ventilation | Exhaust Fan (Toilet) | TEF-B.11 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0608 | ventilation | Exhaust Fan (Toilet) | TEF-B.12 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0609 | ventilation | Exhaust Fan (Toilet) | TEF-B.12 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0610 | ventilation | Exhaust Fan (Toilet) | TEF-B.12 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0611 | ventilation | Exhaust Fan (Toilet) | TEF-B.13 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0612 | ventilation | Exhaust Fan (Toilet) | TEF-B.13 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0613 | ventilation | Exhaust Fan (Toilet) | TEF-B.13 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0614 | ventilation | Exhaust Fan (Toilet) | TEF-B.14 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0615 | ventilation | Exhaust Fan (Toilet) | TEF-B.14 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0616 | ventilation | Exhaust Fan (Toilet) | TEF-B.14 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0617 | ventilation | Exhaust Fan (Toilet) | TEF-B.15 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0618 | ventilation | Exhaust Fan (Toilet) | TEF-B.15 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0619 | ventilation | Exhaust Fan (Toilet) | TEF-B.15 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0620 | ventilation | Exhaust Fan (Toilet) | TEF-B.16 | Basement 1 | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0621 | ventilation | Exhaust Fan (Toilet) | TEF-B.16 | Basement 1 | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0622 | ventilation | Exhaust Fan (Toilet) | TEF-B.16 | Basement 1 | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-B1 | BMS Points list (TUEC) + ME/PL Points list
P0623 | ventilation | Exhaust Fan (Toilet) | TEF-RD.1 | Roof Deck | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0624 | ventilation | Exhaust Fan (Toilet) | TEF-RD.1 | Roof Deck | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0625 | ventilation | Exhaust Fan (Toilet) | TEF-RD.1 | Roof Deck | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0626 | ventilation | Exhaust Fan (Toilet) | TEF-RD.2 | Roof Deck | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0627 | ventilation | Exhaust Fan (Toilet) | TEF-RD.2 | Roof Deck | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0628 | ventilation | Exhaust Fan (Toilet) | TEF-RD.2 | Roof Deck | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0629 | ventilation | Exhaust Fan (Toilet) | TEF-RD.3 | Roof Deck | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0630 | ventilation | Exhaust Fan (Toilet) | TEF-RD.3 | Roof Deck | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0631 | ventilation | Exhaust Fan (Toilet) | TEF-RD.3 | Roof Deck | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0632 | ventilation | Exhaust Fan (General) | EF-1.2A | Ground Floor Lobby | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0633 | ventilation | Exhaust Fan (General) | EF-1.2A | Ground Floor Lobby | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0634 | ventilation | Exhaust Fan (General) | EF-1.2A | Ground Floor Lobby | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0635 | ventilation | Exhaust Fan (General) | EF-LPG.1 | Ground Floor Lobby | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0636 | ventilation | Exhaust Fan (General) | EF-LPG.1 | Ground Floor Lobby | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0637 | ventilation | Exhaust Fan (General) | EF-LPG.1 | Ground Floor Lobby | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0638 | ventilation | Exhaust Fan (General) | EF-1MR.1 | Ground Floor Lobby | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0639 | ventilation | Exhaust Fan (General) | EF-1MR.1 | Ground Floor Lobby | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0640 | ventilation | Exhaust Fan (General) | EF-1MR.1 | Ground Floor Lobby | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0641 | ventilation | Exhaust Fan (General) | EF-1STO.1 | Ground Floor Lobby | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0642 | ventilation | Exhaust Fan (General) | EF-1STO.1 | Ground Floor Lobby | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0643 | ventilation | Exhaust Fan (General) | EF-1STO.1 | Ground Floor Lobby | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0644 | ventilation | Exhaust Fan (General) | EF-MRF.1 | Ground Floor Lobby | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0645 | ventilation | Exhaust Fan (General) | EF-MRF.1 | Ground Floor Lobby | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0646 | ventilation | Exhaust Fan (General) | EF-MRF.1 | Ground Floor Lobby | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0647 | ventilation | Exhaust Fan (General) | EF-RD.1 | Roof Deck | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0648 | ventilation | Exhaust Fan (General) | EF-RD.1 | Roof Deck | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0649 | ventilation | Exhaust Fan (General) | EF-RD.1 | Roof Deck | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0650 | ventilation | Exhaust Fan (General) | EF-RD.2 | Roof Deck | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0651 | ventilation | Exhaust Fan (General) | EF-RD.2 | Roof Deck | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0652 | ventilation | Exhaust Fan (General) | EF-RD.2 | Roof Deck | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0653 | ventilation | Exhaust Fan (General) | EF-1 | Roof Deck | Fan motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0654 | ventilation | Exhaust Fan (General) | EF-1 | Roof Deck | Fan H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0655 | ventilation | Exhaust Fan (General) | EF-1 | Roof Deck | Fan trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0656 | hot_water | Calorifier (Hot Water Storage Tank) | HWT-LZ-1 | Lower Ground HW Plant | Tank temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0657 | hot_water | Heat Pump | HP-LZ-1 | Lower Ground HW Plant | Pump motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0658 | hot_water | Heat Pump | HP-LZ-1 | Lower Ground HW Plant | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0659 | hot_water | Heat Pump | HP-LZ-1 | Lower Ground HW Plant | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0660 | hot_water | Recirculating Pump | RP-LZ-1 | Lower Ground HW Plant | Pump motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0661 | hot_water | Recirculating Pump | RP-LZ-1 | Lower Ground HW Plant | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0662 | hot_water | Recirculating Pump | RP-LZ-1 | Lower Ground HW Plant | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0663 | hot_water | Calorifier (Hot Water Storage Tank) | HWT-LZ-2 | Lower Ground HW Plant | Tank temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0664 | hot_water | Heat Pump | HP-LZ-2 | Lower Ground HW Plant | Pump motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0665 | hot_water | Heat Pump | HP-LZ-2 | Lower Ground HW Plant | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0666 | hot_water | Heat Pump | HP-LZ-2 | Lower Ground HW Plant | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0667 | hot_water | Recirculating Pump | RP-LZ-2 | Lower Ground HW Plant | Pump motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0668 | hot_water | Recirculating Pump | RP-LZ-2 | Lower Ground HW Plant | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0669 | hot_water | Recirculating Pump | RP-LZ-2 | Lower Ground HW Plant | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0670 | hot_water | Calorifier (Hot Water Storage Tank) | HWT-LZ-3 | Lower Ground HW Plant | Tank temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0671 | hot_water | Heat Pump | HP-LZ-3 | Lower Ground HW Plant | Pump motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0672 | hot_water | Heat Pump | HP-LZ-3 | Lower Ground HW Plant | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0673 | hot_water | Heat Pump | HP-LZ-3 | Lower Ground HW Plant | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0674 | hot_water | Recirculating Pump | RP-LZ-3 | Lower Ground HW Plant | Pump motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0675 | hot_water | Recirculating Pump | RP-LZ-3 | Lower Ground HW Plant | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0676 | hot_water | Recirculating Pump | RP-LZ-3 | Lower Ground HW Plant | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0677 | hot_water | Calorifier (Hot Water Storage Tank) | HWT-HZ-1 | Roof Deck HW Plant | Tank temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0678 | hot_water | Heat Pump | HP-HZ-1 | Roof Deck HW Plant | Pump motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0679 | hot_water | Heat Pump | HP-HZ-1 | Roof Deck HW Plant | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0680 | hot_water | Heat Pump | HP-HZ-1 | Roof Deck HW Plant | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0681 | hot_water | Recirculating Pump | RP-HZ-1 | Roof Deck HW Plant | Pump motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0682 | hot_water | Recirculating Pump | RP-HZ-1 | Roof Deck HW Plant | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0683 | hot_water | Recirculating Pump | RP-HZ-1 | Roof Deck HW Plant | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0684 | hot_water | Calorifier (Hot Water Storage Tank) | HWT-HZ-2 | Roof Deck HW Plant | Tank temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0685 | hot_water | Heat Pump | HP-HZ-2 | Roof Deck HW Plant | Pump motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0686 | hot_water | Heat Pump | HP-HZ-2 | Roof Deck HW Plant | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0687 | hot_water | Heat Pump | HP-HZ-2 | Roof Deck HW Plant | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0688 | hot_water | Recirculating Pump | RP-HZ-2 | Roof Deck HW Plant | Pump motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0689 | hot_water | Recirculating Pump | RP-HZ-2 | Roof Deck HW Plant | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0690 | hot_water | Recirculating Pump | RP-HZ-2 | Roof Deck HW Plant | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0691 | hot_water | Calorifier (Hot Water Storage Tank) | HWT-HZ-3 | Roof Deck HW Plant | Tank temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0692 | hot_water | Heat Pump | HP-HZ-3 | Roof Deck HW Plant | Pump motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0693 | hot_water | Heat Pump | HP-HZ-3 | Roof Deck HW Plant | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0694 | hot_water | Heat Pump | HP-HZ-3 | Roof Deck HW Plant | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0695 | hot_water | Recirculating Pump | RP-HZ-3 | Roof Deck HW Plant | Pump motor status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0696 | hot_water | Recirculating Pump | RP-HZ-3 | Roof Deck HW Plant | Pump motor H/O/A status | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0697 | hot_water | Recirculating Pump | RP-HZ-3 | Roof Deck HW Plant | Pump motor trip alarm | DI | Auxiliary Contact | Equipment Supplier |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list
P0698 | hot_water | Hot Water Header Set | HW-HEADERS | Lower Ground HW Plant | HW supply header temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0699 | hot_water | Hot Water Header Set | HW-HEADERS | Lower Ground HW Plant | Make-up cold water header temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0700 | hot_water | Hot Water Header Set | HW-HEADERS | Lower Ground HW Plant | HW return temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0701 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Supply steam pressure | AI | Pressure Transmitter | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0702 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Low water level alarm | HLI | Equipment Supplier level sensor | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0703 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | High water level alarm | HLI | Equipment Supplier level sensor | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0704 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Burner power | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0705 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Small-fire control signal | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0706 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Big-fire control signal | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0707 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Burner status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0708 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Burner-fire running status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0709 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Blower motor status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0710 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Fuel-oil pump status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0711 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Waterfeed pump status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0712 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Burner trip alarm | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0713 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Blower trip alarm | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0714 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Oil pump trip alarm | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0715 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Motorized blowdown valve command | AO | Electric Valve Actuator | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0716 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Motorized blowdown valve status | DI | Auxiliary Contact | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0717 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Feedwater supply temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0718 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Fluegas temperature | AI | Temperature Sensor (high-temp) | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0719 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Fluegas oxygen level | AI | Oxygen Sensor | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0720 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Steam supply pressure (high alarm) | AI | Pressure Transmitter | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0721 | steam | Steam Boiler | SB-1 | Lower Ground Laundry | Boiler firing-rate command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0722 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Supply steam pressure | AI | Pressure Transmitter | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0723 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Low water level alarm | HLI | Equipment Supplier level sensor | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0724 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | High water level alarm | HLI | Equipment Supplier level sensor | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0725 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Burner power | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0726 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Small-fire control signal | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0727 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Big-fire control signal | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0728 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Burner status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0729 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Burner-fire running status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0730 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Blower motor status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0731 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Fuel-oil pump status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0732 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Waterfeed pump status | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0733 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Burner trip alarm | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0734 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Blower trip alarm | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0735 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Oil pump trip alarm | HLI | — | Equipment Supplier |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0736 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Motorized blowdown valve command | AO | Electric Valve Actuator | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0737 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Motorized blowdown valve status | DI | Auxiliary Contact | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0738 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Feedwater supply temperature | AI | Temperature Sensor | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0739 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Fluegas temperature | AI | Temperature Sensor (high-temp) | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0740 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Fluegas oxygen level | AI | Oxygen Sensor | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0741 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Steam supply pressure (high alarm) | AI | Pressure Transmitter | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0742 | steam | Steam Boiler | SB-2 | Lower Ground Laundry | Boiler firing-rate command | AO | 0-10V / 4-20 mA | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0743 | power_metering | Multifunction Power Meter (Main) | PM-MAIN | Main Switchgear Room | Main power meter (kW, kWh, V, A, PF, kVAR) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0744 | power_metering | Multifunction Power Meter (Feeder) | PM-CHILLER-1 | 2nd Level Mechanical Room | Feeder power meter (kW, kWh, V, A) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0745 | power_metering | Multifunction Power Meter (Feeder) | PM-CHILLER-2 | 2nd Level Mechanical Room | Feeder power meter (kW, kWh, V, A) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0746 | power_metering | Multifunction Power Meter (Feeder) | PM-CHILLER-3 | 2nd Level Mechanical Room | Feeder power meter (kW, kWh, V, A) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-LG-CHILLER | BMS Points list (TUEC) + ME/PL Points list
P0747 | power_metering | Multifunction Power Meter (Feeder) | PM-CASINO-FB | 2nd Floor Casino | Feeder power meter (kW, kWh, V, A) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0748 | power_metering | Multifunction Power Meter (Feeder) | PM-KITCHEN-2F | 2nd Floor BOH | Feeder power meter (kW, kWh, V, A) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-2F-CASINO | BMS Points list (TUEC) + ME/PL Points list
P0749 | power_metering | Multifunction Power Meter (Feeder) | PM-LOBBY-GF | Ground Floor | Feeder power meter (kW, kWh, V, A) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0750 | power_metering | Multifunction Power Meter (Feeder) | PM-ELEVATOR | Ground Floor | Feeder power meter (kW, kWh, V, A) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-GF | BMS Points list (TUEC) + ME/PL Points list
P0751 | power_metering | Multifunction Power Meter (Feeder) | PM-LIGHTING-GUEST | 3rd Floor Amenity | Feeder power meter (kW, kWh, V, A) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-3F | BMS Points list (TUEC) + ME/PL Points list
P0752 | power_metering | Multifunction Power Meter (Feeder) | PM-LAUNDRY-LG | Lower Ground Laundry | Feeder power meter (kW, kWh, V, A) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-LG-PLUMB | BMS Points list (TUEC) + ME/PL Points list
P0753 | power_metering | Multifunction Power Meter (Feeder) | PM-ROOFDECK-MECH | Roof Deck Mechanical | Feeder power meter (kW, kWh, V, A) | Network | Modbus RTU/TCP | BMS Contractor |  | BMS-PNL-RD-MECH | BMS Points list (TUEC) + ME/PL Points list