## Summary
A2 — Equipment Takeoff Summary
Total instances | 132
By equipment class
Exhaust Fan (Toilet) | 53
Multifunction Power Meter (Feeder) | 10
Exhaust Fan (General) | 8
Precooled Air Handling Unit | 7
Heat Pump | 6
Calorifier (Hot Water Storage Tank) | 6
Recirculating Pump | 6
BTU Meter | 5
AHU (Chilled-Water-Served) | 4
Chiller (Package Water-Cooled) | 3
Cooling Tower | 3
Condenser Water Pump | 3
DOAS Unit | 3
Primary CHW Pump | 3
AHU (Modulating CHW-served) | 2
Ozone Generator (UV-light or Corona) | 2
Steam Boiler | 2
CHW Bypass Header | 1
CHW Return Main Header | 1
CHW Supply Main Header | 1
Cooling Tower (Common) | 1
Hot Water Header Set | 1
Multifunction Power Meter (Main) | 1
By location
3rd Floor Amenity | 26
2nd Level Mechanical Room | 20
Basement 1 | 16
Roof Deck Mechanical | 14
Lower Ground HW Plant | 10
Ground Floor Lobby | 9
Roof Deck HW Plant | 9
Roof Deck | 6
2nd Floor BOH | 5
Ground Floor | 4
2nd Floor Casino MVAC Room | 3
2nd Floor Casino | 3
Lower Ground Laundry | 3
Basement 1 BOH | 1
Ground Floor BOH | 1
Ground Floor Mezzanine BOH | 1
Main Switchgear Room | 1
By panel
BMS-PNL-3F | 26
BMS-PNL-RD-MECH | 25
BMS-PNL-LG-CHILLER | 20
BMS-PNL-B1 | 17
BMS-PNL-GF | 16
BMS-PNL-LG-PLUMB | 13
BMS-PNL-2F-CASINO | 11
BMS-PNL-RD-CT | 4

## Equipment Takeoff
ID | Equipment Class | Quantity | Location | System | Panel | Primary C/O | Physical I/O | HLI Subpoints | Network Drops | Total I/O | Make/Model Assumed | Network Type | Typical Supplier | Notes
AHU-2F-1 | AHU (Chilled-Water-Served) | 1 | 2nd Floor BOH | common_area | BMS-PNL-2F-CASINO | BMS Contractor | 15 | 1 | 0 | 16 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-2M.1 | AHU (Modulating CHW-served) | 1 | 2nd Floor Casino MVAC Room | casino_mvac | BMS-PNL-2F-CASINO | BMS Contractor | 16 | 1 | 0 | 17 | Modulating CHW-served AHU with VFD, modulating valve and dampers (position feedback) | Hardwired (VFD via BACnet HLI) | Mechanical contractor | Casino-spec AHU — modulating actuators with position feedback; CO/CO2 monitoring at return duct.
AHU-2M.2 | AHU (Modulating CHW-served) | 1 | 2nd Floor Casino MVAC Room | casino_mvac | BMS-PNL-2F-CASINO | BMS Contractor | 16 | 1 | 0 | 17 | Modulating CHW-served AHU with VFD, modulating valve and dampers (position feedback) | Hardwired (VFD via BACnet HLI) | Mechanical contractor | Casino-spec AHU — modulating actuators with position feedback; CO/CO2 monitoring at return duct.
AHU-B1-1 | AHU (Chilled-Water-Served) | 1 | Basement 1 BOH | common_area | BMS-PNL-B1 | BMS Contractor | 15 | 1 | 0 | 16 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-GF-1 | AHU (Chilled-Water-Served) | 1 | Ground Floor BOH | common_area | BMS-PNL-GF | BMS Contractor | 15 | 1 | 0 | 16 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-GFM-1 | AHU (Chilled-Water-Served) | 1 | Ground Floor Mezzanine BOH | common_area | BMS-PNL-GF | BMS Contractor | 15 | 1 | 0 | 16 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
BTU-1 | BTU Meter | 1 | 2nd Level Mechanical Room | btu_metering | BMS-PNL-LG-CHILLER | BMS Contractor | 0 | 0 | 1 | 1 | Ultrasonic or insertion-type BTU meter with Modbus output (Onicon, Aichi, Kamstrup) | Modbus RTU/TCP | BMS contractor | System-level energy submeter.
BTU-2 | BTU Meter | 1 | 2nd Level Mechanical Room | btu_metering | BMS-PNL-LG-CHILLER | BMS Contractor | 0 | 0 | 1 | 1 | Ultrasonic or insertion-type BTU meter with Modbus output (Onicon, Aichi, Kamstrup) | Modbus RTU/TCP | BMS contractor | System-level energy submeter.
BTU-3 | BTU Meter | 1 | 2nd Level Mechanical Room | btu_metering | BMS-PNL-LG-CHILLER | BMS Contractor | 0 | 0 | 1 | 1 | Ultrasonic or insertion-type BTU meter with Modbus output (Onicon, Aichi, Kamstrup) | Modbus RTU/TCP | BMS contractor | System-level energy submeter.
BTU-4 | BTU Meter | 1 | 2nd Level Mechanical Room | btu_metering | BMS-PNL-LG-CHILLER | BMS Contractor | 0 | 0 | 1 | 1 | Ultrasonic or insertion-type BTU meter with Modbus output (Onicon, Aichi, Kamstrup) | Modbus RTU/TCP | BMS contractor | System-level energy submeter.
BTU-5 | BTU Meter | 1 | 2nd Level Mechanical Room | btu_metering | BMS-PNL-LG-CHILLER | BMS Contractor | 0 | 0 | 1 | 1 | Ultrasonic or insertion-type BTU meter with Modbus output (Onicon, Aichi, Kamstrup) | Modbus RTU/TCP | BMS contractor | System-level energy submeter.
CH-1 | Chiller (Package Water-Cooled) | 1 | 2nd Level Mechanical Room | chilled_water | BMS-PNL-LG-CHILLER | Equipment Supplier | 9 | 18 | 1 | 28 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CH-2 | Chiller (Package Water-Cooled) | 1 | 2nd Level Mechanical Room | chilled_water | BMS-PNL-LG-CHILLER | Equipment Supplier | 9 | 18 | 1 | 28 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CH-3 | Chiller (Package Water-Cooled) | 1 | 2nd Level Mechanical Room | chilled_water | BMS-PNL-LG-CHILLER | Equipment Supplier | 9 | 18 | 1 | 28 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CHW-BYPASS | CHW Bypass Header | 1 | 2nd Level Mechanical Room | chilled_water | BMS-PNL-LG-CHILLER | BMS Contractor | 5 | 0 | 0 | 5 | BMS dP/dT sensors + motorized bypass valve (BMS-supplied) | Hardwired | BMS contractor | BMS controls bypass valve to maintain CHW differential.
CHW-HDR-R | CHW Return Main Header | 1 | 2nd Level Mechanical Room | chilled_water | BMS-PNL-LG-CHILLER | BMS Contractor | 2 | 0 | 0 | 2 | BMS T+P sensors on CHW return manifold | Hardwired | BMS contractor | Field instrumentation only.
CHW-HDR-S | CHW Supply Main Header | 1 | 2nd Level Mechanical Room | chilled_water | BMS-PNL-LG-CHILLER | BMS Contractor | 2 | 0 | 0 | 2 | BMS T+P sensors on CHW supply manifold | Hardwired | BMS contractor | Field instrumentation only.
CT-1 | Cooling Tower | 1 | Roof Deck Mechanical | condenser_water | BMS-PNL-RD-CT | BMS Contractor | 12 | 0 | 0 | 12 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-2 | Cooling Tower | 1 | Roof Deck Mechanical | condenser_water | BMS-PNL-RD-CT | BMS Contractor | 12 | 0 | 0 | 12 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-3 | Cooling Tower | 1 | Roof Deck Mechanical | condenser_water | BMS-PNL-RD-CT | BMS Contractor | 12 | 0 | 0 | 12 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-COMMON | Cooling Tower (Common) | 1 | Roof Deck Mechanical | condenser_water | BMS-PNL-RD-CT | BMS Contractor | 4 | 0 | 0 | 4 | Common BMS sensors at cooling tower area (OA T/RH, condenser headers) | Hardwired | BMS contractor | Field instrumentation only — no equipment per se.
CWP-1 | Condenser Water Pump | 1 | 2nd Level Mechanical Room | chilled_water | BMS-PNL-LG-CHILLER | Equipment Supplier | 5 | 1 | 0 | 6 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
CWP-2 | Condenser Water Pump | 1 | 2nd Level Mechanical Room | chilled_water | BMS-PNL-LG-CHILLER | Equipment Supplier | 5 | 1 | 0 | 6 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
CWP-3 | Condenser Water Pump | 1 | 2nd Level Mechanical Room | chilled_water | BMS-PNL-LG-CHILLER | Equipment Supplier | 5 | 1 | 0 | 6 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
DOAS-2F-CASINO | DOAS Unit | 1 | 2nd Floor Casino MVAC Room | ventilation | BMS-PNL-2F-CASINO | BMS Contractor | 24 | 1 | 1 | 26 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
DOAS-RD1 | DOAS Unit | 1 | Roof Deck Mechanical | ventilation | BMS-PNL-RD-MECH | BMS Contractor | 24 | 1 | 1 | 26 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
DOAS-RD2 | DOAS Unit | 1 | Roof Deck Mechanical | ventilation | BMS-PNL-RD-MECH | BMS Contractor | 24 | 1 | 1 | 26 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
EF-1 | Exhaust Fan (General) | 1 | Roof Deck | ventilation | BMS-PNL-RD-MECH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-1.2A | Exhaust Fan (General) | 1 | Ground Floor Lobby | ventilation | BMS-PNL-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-1MR.1 | Exhaust Fan (General) | 1 | Ground Floor Lobby | ventilation | BMS-PNL-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-1STO.1 | Exhaust Fan (General) | 1 | Ground Floor Lobby | ventilation | BMS-PNL-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-LPG.1 | Exhaust Fan (General) | 1 | Ground Floor Lobby | ventilation | BMS-PNL-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-MRF.1 | Exhaust Fan (General) | 1 | Ground Floor Lobby | ventilation | BMS-PNL-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-RD.1 | Exhaust Fan (General) | 1 | Roof Deck | ventilation | BMS-PNL-RD-MECH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-RD.2 | Exhaust Fan (General) | 1 | Roof Deck | ventilation | BMS-PNL-RD-MECH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
HP-HZ-1 | Heat Pump | 1 | Roof Deck HW Plant | hot_water | BMS-PNL-RD-MECH | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-HZ-2 | Heat Pump | 1 | Roof Deck HW Plant | hot_water | BMS-PNL-RD-MECH | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-HZ-3 | Heat Pump | 1 | Roof Deck HW Plant | hot_water | BMS-PNL-RD-MECH | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-LZ-1 | Heat Pump | 1 | Lower Ground HW Plant | hot_water | BMS-PNL-LG-PLUMB | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-LZ-2 | Heat Pump | 1 | Lower Ground HW Plant | hot_water | BMS-PNL-LG-PLUMB | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-LZ-3 | Heat Pump | 1 | Lower Ground HW Plant | hot_water | BMS-PNL-LG-PLUMB | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HW-HEADERS | Hot Water Header Set | 1 | Lower Ground HW Plant | hot_water | BMS-PNL-LG-PLUMB | BMS Contractor | 3 | 0 | 0 | 3 | Hot water supply/return manifolds with BMS T sensors and make-up cold water T sensor | Hardwired | BMS contractor | Field instrumentation on existing piping.
HWT-HZ-1 | Calorifier (Hot Water Storage Tank) | 1 | Roof Deck HW Plant | hot_water | BMS-PNL-RD-MECH | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-HZ-2 | Calorifier (Hot Water Storage Tank) | 1 | Roof Deck HW Plant | hot_water | BMS-PNL-RD-MECH | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-HZ-3 | Calorifier (Hot Water Storage Tank) | 1 | Roof Deck HW Plant | hot_water | BMS-PNL-RD-MECH | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-LZ-1 | Calorifier (Hot Water Storage Tank) | 1 | Lower Ground HW Plant | hot_water | BMS-PNL-LG-PLUMB | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-LZ-2 | Calorifier (Hot Water Storage Tank) | 1 | Lower Ground HW Plant | hot_water | BMS-PNL-LG-PLUMB | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-LZ-3 | Calorifier (Hot Water Storage Tank) | 1 | Lower Ground HW Plant | hot_water | BMS-PNL-LG-PLUMB | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
ION-2F-1 | Ozone Generator (UV-light or Corona) | 1 | 2nd Floor Casino | casino_mvac | BMS-PNL-2F-CASINO | Equipment Supplier | 2 | 0 | 0 | 2 | UV-light or corona-discharge ozone generator (paired with Casino AHU) | Hardwired | Equipment supplier | Casino-specific air-treatment device. BMS monitors status/trip and reads VOC sensor (BMS-supplied).
ION-2F-2 | Ozone Generator (UV-light or Corona) | 1 | 2nd Floor Casino | casino_mvac | BMS-PNL-2F-CASINO | Equipment Supplier | 2 | 0 | 0 | 2 | UV-light or corona-discharge ozone generator (paired with Casino AHU) | Hardwired | Equipment supplier | Casino-specific air-treatment device. BMS monitors status/trip and reads VOC sensor (BMS-supplied).
PAHU-01 | Precooled Air Handling Unit | 1 | Roof Deck Mechanical | ventilation | BMS-PNL-RD-MECH | BMS Contractor | 14 | 1 | 1 | 16 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-02 | Precooled Air Handling Unit | 1 | Roof Deck Mechanical | ventilation | BMS-PNL-RD-MECH | BMS Contractor | 14 | 1 | 1 | 16 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-03 | Precooled Air Handling Unit | 1 | Roof Deck Mechanical | ventilation | BMS-PNL-RD-MECH | BMS Contractor | 14 | 1 | 1 | 16 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-04 | Precooled Air Handling Unit | 1 | Roof Deck Mechanical | ventilation | BMS-PNL-RD-MECH | BMS Contractor | 14 | 1 | 1 | 16 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-05 | Precooled Air Handling Unit | 1 | Roof Deck Mechanical | ventilation | BMS-PNL-RD-MECH | BMS Contractor | 14 | 1 | 1 | 16 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-06 | Precooled Air Handling Unit | 1 | Roof Deck Mechanical | ventilation | BMS-PNL-RD-MECH | BMS Contractor | 14 | 1 | 1 | 16 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-07 | Precooled Air Handling Unit | 1 | Roof Deck Mechanical | ventilation | BMS-PNL-RD-MECH | BMS Contractor | 14 | 1 | 1 | 16 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PCHWP-1 | Primary CHW Pump | 1 | 2nd Level Mechanical Room | chilled_water | BMS-PNL-LG-CHILLER | Equipment Supplier | 7 | 1 | 0 | 8 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
PCHWP-2 | Primary CHW Pump | 1 | 2nd Level Mechanical Room | chilled_water | BMS-PNL-LG-CHILLER | Equipment Supplier | 7 | 1 | 0 | 8 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
PCHWP-3 | Primary CHW Pump | 1 | 2nd Level Mechanical Room | chilled_water | BMS-PNL-LG-CHILLER | Equipment Supplier | 7 | 1 | 0 | 8 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
PM-CASINO-FB | Multifunction Power Meter (Feeder) | 1 | 2nd Floor Casino | power_metering | BMS-PNL-2F-CASINO | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-CHILLER-1 | Multifunction Power Meter (Feeder) | 1 | 2nd Level Mechanical Room | power_metering | BMS-PNL-LG-CHILLER | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-CHILLER-2 | Multifunction Power Meter (Feeder) | 1 | 2nd Level Mechanical Room | power_metering | BMS-PNL-LG-CHILLER | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-CHILLER-3 | Multifunction Power Meter (Feeder) | 1 | 2nd Level Mechanical Room | power_metering | BMS-PNL-LG-CHILLER | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-ELEVATOR | Multifunction Power Meter (Feeder) | 1 | Ground Floor | power_metering | BMS-PNL-GF | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-KITCHEN-2F | Multifunction Power Meter (Feeder) | 1 | 2nd Floor BOH | power_metering | BMS-PNL-2F-CASINO | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-LAUNDRY-LG | Multifunction Power Meter (Feeder) | 1 | Lower Ground Laundry | power_metering | BMS-PNL-LG-PLUMB | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-LIGHTING-GUEST | Multifunction Power Meter (Feeder) | 1 | 3rd Floor Amenity | power_metering | BMS-PNL-3F | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-LOBBY-GF | Multifunction Power Meter (Feeder) | 1 | Ground Floor | power_metering | BMS-PNL-GF | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
PM-MAIN | Multifunction Power Meter (Main) | 1 | Main Switchgear Room | power_metering | BMS-PNL-GF | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output (Schneider PM-series, ABB M2M, Siemens SENTRON), main switchgear class | Modbus RTU/TCP | BMS contractor | Mounted in main switchgear or on dedicated BMS-side panel.
PM-ROOFDECK-MECH | Multifunction Power Meter (Feeder) | 1 | Roof Deck Mechanical | power_metering | BMS-PNL-RD-MECH | BMS Contractor | 0 | 0 | 1 | 1 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
RP-HZ-1 | Recirculating Pump | 1 | Roof Deck HW Plant | hot_water | BMS-PNL-RD-MECH | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-HZ-2 | Recirculating Pump | 1 | Roof Deck HW Plant | hot_water | BMS-PNL-RD-MECH | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-HZ-3 | Recirculating Pump | 1 | Roof Deck HW Plant | hot_water | BMS-PNL-RD-MECH | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-LZ-1 | Recirculating Pump | 1 | Lower Ground HW Plant | hot_water | BMS-PNL-LG-PLUMB | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-LZ-2 | Recirculating Pump | 1 | Lower Ground HW Plant | hot_water | BMS-PNL-LG-PLUMB | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-LZ-3 | Recirculating Pump | 1 | Lower Ground HW Plant | hot_water | BMS-PNL-LG-PLUMB | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
SB-1 | Steam Boiler | 1 | Lower Ground Laundry | steam | BMS-PNL-LG-PLUMB | Equipment Supplier | 8 | 13 | 0 | 21 | Fire-tube steam boiler with multi-stage burner, fuel-oil fired (typical for hotel laundry) | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies steam pressure, feedwater T, fluegas T+O2 sensors. Boiler equipment provides aux contacts for status/HOA/trip points.
SB-2 | Steam Boiler | 1 | Lower Ground Laundry | steam | BMS-PNL-LG-PLUMB | Equipment Supplier | 8 | 13 | 0 | 21 | Fire-tube steam boiler with multi-stage burner, fuel-oil fired (typical for hotel laundry) | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies steam pressure, feedwater T, fluegas T+O2 sensors. Boiler equipment provides aux contacts for status/HOA/trip points.
TEF-1.1 | Exhaust Fan (Toilet) | 1 | Ground Floor Lobby | ventilation | BMS-PNL-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-1.2 | Exhaust Fan (Toilet) | 1 | Ground Floor Lobby | ventilation | BMS-PNL-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-1.3 | Exhaust Fan (Toilet) | 1 | Ground Floor Lobby | ventilation | BMS-PNL-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-1.4 | Exhaust Fan (Toilet) | 1 | Ground Floor Lobby | ventilation | BMS-PNL-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2.1 | Exhaust Fan (Toilet) | 1 | 2nd Floor BOH | ventilation | BMS-PNL-2F-CASINO | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2.3 | Exhaust Fan (Toilet) | 1 | 2nd Floor BOH | ventilation | BMS-PNL-2F-CASINO | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2B.3 | Exhaust Fan (Toilet) | 1 | 2nd Floor BOH | ventilation | BMS-PNL-2F-CASINO | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3A.1 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3A.2 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3B | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3C.1 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3C.2 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.1 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.10 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.11 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.12 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.13 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.14 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.15 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.16 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.17 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.18 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.19 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.2 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.20 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.3 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.4 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.5 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.6 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.7 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.8 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.9 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity | ventilation | BMS-PNL-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.1 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.10 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.11 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.12 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.13 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.14 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.15 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.16 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.2 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.3 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.4 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.5 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.6 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.7 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.8 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.9 | Exhaust Fan (Toilet) | 1 | Basement 1 | ventilation | BMS-PNL-B1 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-GS.1 | Exhaust Fan (Toilet) | 1 | Ground Floor | ventilation | BMS-PNL-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-GS.2 | Exhaust Fan (Toilet) | 1 | Ground Floor | ventilation | BMS-PNL-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-RD.1 | Exhaust Fan (Toilet) | 1 | Roof Deck | ventilation | BMS-PNL-RD-MECH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-RD.2 | Exhaust Fan (Toilet) | 1 | Roof Deck | ventilation | BMS-PNL-RD-MECH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-RD.3 | Exhaust Fan (Toilet) | 1 | Roof Deck | ventilation | BMS-PNL-RD-MECH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.