## Summary
A3 — Cable Schedule Summary
Total field cable runs | 194
Total field cable length (m) | 3409
Total trunk cable length (m) | 1480
Total power feed length (m) | 144
GRAND TOTAL cable length (m) | 5033
By cable type (m)
Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3409

## Field Cables
ID | From | To | Equipment Class | System | Location | Cable Type | Conductors Required | Conductors Specified | Length (m) | I/O Points Carried | Notes
C0001 | BMS-PNL-2F-CASINO | AHU-2F-1 (BMS Contractor) | AHU (Chilled-Water-Served) | common_area | 2nd Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 8 | 8 | 22 | 7 | 7 I/O points carried, 8C cable; length 22 m (typical_range:boh_same_floor)
C0002 | BMS-PNL-2F-CASINO | AHU-2F-1 (Equipment Supplier) | AHU (Chilled-Water-Served) | common_area | 2nd Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 22 | 5 | 5 I/O points carried, 6C cable; length 22 m (typical_range:boh_same_floor)
C0003 | BMS-PNL-2F-CASINO | AHU-2F-1 (ME Contractor) | AHU (Chilled-Water-Served) | common_area | 2nd Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0004 | BMS-PNL-2F-CASINO | AHU-2M.1 (BMS Contractor) | AHU (Modulating CHW-served) | casino_mvac | 2nd Floor Casino MVAC Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 9 | 12 | 22 | 8 | 8 I/O points carried, 12C cable; length 22 m (typical_range:boh_same_floor)
C0005 | BMS-PNL-2F-CASINO | AHU-2M.1 (Equipment Supplier) | AHU (Modulating CHW-served) | casino_mvac | 2nd Floor Casino MVAC Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 22 | 5 | 5 I/O points carried, 6C cable; length 22 m (typical_range:boh_same_floor)
C0006 | BMS-PNL-2F-CASINO | AHU-2M.1 (ME Contractor) | AHU (Modulating CHW-served) | casino_mvac | 2nd Floor Casino MVAC Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0007 | BMS-PNL-2F-CASINO | AHU-2M.2 (BMS Contractor) | AHU (Modulating CHW-served) | casino_mvac | 2nd Floor Casino MVAC Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 9 | 12 | 22 | 8 | 8 I/O points carried, 12C cable; length 22 m (typical_range:boh_same_floor)
C0008 | BMS-PNL-2F-CASINO | AHU-2M.2 (Equipment Supplier) | AHU (Modulating CHW-served) | casino_mvac | 2nd Floor Casino MVAC Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 22 | 5 | 5 I/O points carried, 6C cable; length 22 m (typical_range:boh_same_floor)
C0009 | BMS-PNL-2F-CASINO | AHU-2M.2 (ME Contractor) | AHU (Modulating CHW-served) | casino_mvac | 2nd Floor Casino MVAC Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0010 | BMS-PNL-B1 | AHU-B1-1 (BMS Contractor) | AHU (Chilled-Water-Served) | common_area | Basement 1 BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 8 | 8 | 22 | 7 | 7 I/O points carried, 8C cable; length 22 m (typical_range:boh_same_floor)
C0011 | BMS-PNL-B1 | AHU-B1-1 (Equipment Supplier) | AHU (Chilled-Water-Served) | common_area | Basement 1 BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 22 | 5 | 5 I/O points carried, 6C cable; length 22 m (typical_range:boh_same_floor)
C0012 | BMS-PNL-B1 | AHU-B1-1 (ME Contractor) | AHU (Chilled-Water-Served) | common_area | Basement 1 BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0013 | BMS-PNL-GF | AHU-GF-1 (BMS Contractor) | AHU (Chilled-Water-Served) | common_area | Ground Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 8 | 8 | 22 | 7 | 7 I/O points carried, 8C cable; length 22 m (typical_range:boh_same_floor)
C0014 | BMS-PNL-GF | AHU-GF-1 (Equipment Supplier) | AHU (Chilled-Water-Served) | common_area | Ground Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 22 | 5 | 5 I/O points carried, 6C cable; length 22 m (typical_range:boh_same_floor)
C0015 | BMS-PNL-GF | AHU-GF-1 (ME Contractor) | AHU (Chilled-Water-Served) | common_area | Ground Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0016 | BMS-PNL-GF | AHU-GFM-1 (BMS Contractor) | AHU (Chilled-Water-Served) | common_area | Ground Floor Mezzanine BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 8 | 8 | 22 | 7 | 7 I/O points carried, 8C cable; length 22 m (typical_range:boh_same_floor)
C0017 | BMS-PNL-GF | AHU-GFM-1 (Equipment Supplier) | AHU (Chilled-Water-Served) | common_area | Ground Floor Mezzanine BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 22 | 5 | 5 I/O points carried, 6C cable; length 22 m (typical_range:boh_same_floor)
C0018 | BMS-PNL-GF | AHU-GFM-1 (ME Contractor) | AHU (Chilled-Water-Served) | common_area | Ground Floor Mezzanine BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0019 | BMS-PNL-LG-CHILLER | CH-1 (BMS Contractor) | Chiller (Package Water-Cooled) | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 12 | 5 | 5 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0020 | BMS-PNL-LG-CHILLER | CH-1 (ME Contractor) | Chiller (Package Water-Cooled) | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 5 | 6 | 12 | 4 | 4 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0021 | BMS-PNL-LG-CHILLER | CH-2 (BMS Contractor) | Chiller (Package Water-Cooled) | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 12 | 5 | 5 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0022 | BMS-PNL-LG-CHILLER | CH-2 (ME Contractor) | Chiller (Package Water-Cooled) | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 5 | 6 | 12 | 4 | 4 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0023 | BMS-PNL-LG-CHILLER | CH-3 (BMS Contractor) | Chiller (Package Water-Cooled) | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 12 | 5 | 5 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0024 | BMS-PNL-LG-CHILLER | CH-3 (ME Contractor) | Chiller (Package Water-Cooled) | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 5 | 6 | 12 | 4 | 4 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0025 | BMS-PNL-LG-CHILLER | CHW-BYPASS (BMS Contractor) | CHW Bypass Header | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0026 | BMS-PNL-LG-CHILLER | CHW-BYPASS (ME Contractor) | CHW Bypass Header | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0027 | BMS-PNL-LG-CHILLER | CHW-HDR-R (BMS Contractor) | CHW Return Main Header | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0028 | BMS-PNL-LG-CHILLER | CHW-HDR-S (BMS Contractor) | CHW Supply Main Header | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0029 | BMS-PNL-RD-CT | CT-1 (BMS Contractor) | Cooling Tower | condenser_water | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 7 | 8 | 15 | 7 | 7 I/O points carried, 8C cable; length 15 m (typical_range:roofdeck_plant_area)
C0030 | BMS-PNL-RD-CT | CT-1 (Equipment Supplier) | Cooling Tower | condenser_water | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0031 | BMS-PNL-RD-CT | CT-1 (ME Contractor) | Cooling Tower | condenser_water | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0032 | BMS-PNL-RD-CT | CT-2 (BMS Contractor) | Cooling Tower | condenser_water | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 7 | 8 | 15 | 7 | 7 I/O points carried, 8C cable; length 15 m (typical_range:roofdeck_plant_area)
C0033 | BMS-PNL-RD-CT | CT-2 (Equipment Supplier) | Cooling Tower | condenser_water | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0034 | BMS-PNL-RD-CT | CT-2 (ME Contractor) | Cooling Tower | condenser_water | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0035 | BMS-PNL-RD-CT | CT-3 (BMS Contractor) | Cooling Tower | condenser_water | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 7 | 8 | 15 | 7 | 7 I/O points carried, 8C cable; length 15 m (typical_range:roofdeck_plant_area)
C0036 | BMS-PNL-RD-CT | CT-3 (Equipment Supplier) | Cooling Tower | condenser_water | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0037 | BMS-PNL-RD-CT | CT-3 (ME Contractor) | Cooling Tower | condenser_water | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0038 | BMS-PNL-RD-CT | CT-COMMON (BMS Contractor) | Cooling Tower (Common) | condenser_water | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0039 | BMS-PNL-RD-CT | CT-COMMON (ME Contractor) | Cooling Tower (Common) | condenser_water | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0040 | BMS-PNL-LG-CHILLER | CWP-1 (BMS Contractor) | Condenser Water Pump | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0041 | BMS-PNL-LG-CHILLER | CWP-1 (Equipment Supplier) | Condenser Water Pump | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0042 | BMS-PNL-LG-CHILLER | CWP-2 (BMS Contractor) | Condenser Water Pump | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0043 | BMS-PNL-LG-CHILLER | CWP-2 (Equipment Supplier) | Condenser Water Pump | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0044 | BMS-PNL-LG-CHILLER | CWP-3 (BMS Contractor) | Condenser Water Pump | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0045 | BMS-PNL-LG-CHILLER | CWP-3 (Equipment Supplier) | Condenser Water Pump | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0046 | BMS-PNL-2F-CASINO | DOAS-2F-CASINO (BMS Contractor) | DOAS Unit | ventilation | 2nd Floor Casino MVAC Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | 12 | 22 | 11 | 11 I/O points carried, 12C cable; length 22 m (typical_range:boh_same_floor)
C0047 | BMS-PNL-2F-CASINO | DOAS-2F-CASINO (Equipment Supplier) | DOAS Unit | ventilation | 2nd Floor Casino MVAC Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | 12 | 22 | 11 | 11 I/O points carried, 12C cable; length 22 m (typical_range:boh_same_floor)
C0048 | BMS-PNL-2F-CASINO | DOAS-2F-CASINO (ME Contractor) | DOAS Unit | ventilation | 2nd Floor Casino MVAC Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 22 | 2 | 2 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0049 | BMS-PNL-RD-MECH | DOAS-RD1 (BMS Contractor) | DOAS Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | 12 | 15 | 11 | 11 I/O points carried, 12C cable; length 15 m (typical_range:roofdeck_plant_area)
C0050 | BMS-PNL-RD-MECH | DOAS-RD1 (Equipment Supplier) | DOAS Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | 12 | 15 | 11 | 11 I/O points carried, 12C cable; length 15 m (typical_range:roofdeck_plant_area)
C0051 | BMS-PNL-RD-MECH | DOAS-RD1 (ME Contractor) | DOAS Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0052 | BMS-PNL-RD-MECH | DOAS-RD2 (BMS Contractor) | DOAS Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | 12 | 15 | 11 | 11 I/O points carried, 12C cable; length 15 m (typical_range:roofdeck_plant_area)
C0053 | BMS-PNL-RD-MECH | DOAS-RD2 (Equipment Supplier) | DOAS Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | 12 | 15 | 11 | 11 I/O points carried, 12C cable; length 15 m (typical_range:roofdeck_plant_area)
C0054 | BMS-PNL-RD-MECH | DOAS-RD2 (ME Contractor) | DOAS Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0055 | BMS-PNL-RD-MECH | EF-1 (Equipment Supplier) | Exhaust Fan (General) | ventilation | Roof Deck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0056 | BMS-PNL-GF | EF-1.2A (Equipment Supplier) | Exhaust Fan (General) | ventilation | Ground Floor Lobby | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0057 | BMS-PNL-GF | EF-1MR.1 (Equipment Supplier) | Exhaust Fan (General) | ventilation | Ground Floor Lobby | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0058 | BMS-PNL-GF | EF-1STO.1 (Equipment Supplier) | Exhaust Fan (General) | ventilation | Ground Floor Lobby | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0059 | BMS-PNL-GF | EF-LPG.1 (Equipment Supplier) | Exhaust Fan (General) | ventilation | Ground Floor Lobby | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0060 | BMS-PNL-GF | EF-MRF.1 (Equipment Supplier) | Exhaust Fan (General) | ventilation | Ground Floor Lobby | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0061 | BMS-PNL-RD-MECH | EF-RD.1 (Equipment Supplier) | Exhaust Fan (General) | ventilation | Roof Deck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0062 | BMS-PNL-RD-MECH | EF-RD.2 (Equipment Supplier) | Exhaust Fan (General) | ventilation | Roof Deck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0063 | BMS-PNL-RD-MECH | HP-HZ-1 (Equipment Supplier) | Heat Pump | hot_water | Roof Deck HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0064 | BMS-PNL-RD-MECH | HP-HZ-2 (Equipment Supplier) | Heat Pump | hot_water | Roof Deck HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0065 | BMS-PNL-RD-MECH | HP-HZ-3 (Equipment Supplier) | Heat Pump | hot_water | Roof Deck HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0066 | BMS-PNL-LG-PLUMB | HP-LZ-1 (Equipment Supplier) | Heat Pump | hot_water | Lower Ground HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0067 | BMS-PNL-LG-PLUMB | HP-LZ-2 (Equipment Supplier) | Heat Pump | hot_water | Lower Ground HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0068 | BMS-PNL-LG-PLUMB | HP-LZ-3 (Equipment Supplier) | Heat Pump | hot_water | Lower Ground HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0069 | BMS-PNL-LG-PLUMB | HW-HEADERS (BMS Contractor) | Hot Water Header Set | hot_water | Lower Ground HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0070 | BMS-PNL-RD-MECH | HWT-HZ-1 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | hot_water | Roof Deck HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 1 | 4 | 15 | 1 | 1 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0071 | BMS-PNL-RD-MECH | HWT-HZ-2 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | hot_water | Roof Deck HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 1 | 4 | 15 | 1 | 1 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0072 | BMS-PNL-RD-MECH | HWT-HZ-3 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | hot_water | Roof Deck HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 1 | 4 | 15 | 1 | 1 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0073 | BMS-PNL-LG-PLUMB | HWT-LZ-1 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | hot_water | Lower Ground HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0074 | BMS-PNL-LG-PLUMB | HWT-LZ-2 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | hot_water | Lower Ground HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0075 | BMS-PNL-LG-PLUMB | HWT-LZ-3 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | hot_water | Lower Ground HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0076 | BMS-PNL-2F-CASINO | ION-2F-1 (Equipment Supplier) | Ozone Generator (UV-light or Corona) | casino_mvac | 2nd Floor Casino | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 22 | 2 | 2 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0077 | BMS-PNL-2F-CASINO | ION-2F-2 (Equipment Supplier) | Ozone Generator (UV-light or Corona) | casino_mvac | 2nd Floor Casino | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 22 | 2 | 2 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0078 | BMS-PNL-RD-MECH | PAHU-01 (BMS Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 8 | 8 | 15 | 7 | 7 I/O points carried, 8C cable; length 15 m (typical_range:roofdeck_plant_area)
C0079 | BMS-PNL-RD-MECH | PAHU-01 (Equipment Supplier) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 15 | 5 | 5 I/O points carried, 6C cable; length 15 m (typical_range:roofdeck_plant_area)
C0080 | BMS-PNL-RD-MECH | PAHU-01 (ME Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0081 | BMS-PNL-RD-MECH | PAHU-02 (BMS Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 8 | 8 | 15 | 7 | 7 I/O points carried, 8C cable; length 15 m (typical_range:roofdeck_plant_area)
C0082 | BMS-PNL-RD-MECH | PAHU-02 (Equipment Supplier) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 15 | 5 | 5 I/O points carried, 6C cable; length 15 m (typical_range:roofdeck_plant_area)
C0083 | BMS-PNL-RD-MECH | PAHU-02 (ME Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0084 | BMS-PNL-RD-MECH | PAHU-03 (BMS Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 8 | 8 | 15 | 7 | 7 I/O points carried, 8C cable; length 15 m (typical_range:roofdeck_plant_area)
C0085 | BMS-PNL-RD-MECH | PAHU-03 (Equipment Supplier) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 15 | 5 | 5 I/O points carried, 6C cable; length 15 m (typical_range:roofdeck_plant_area)
C0086 | BMS-PNL-RD-MECH | PAHU-03 (ME Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0087 | BMS-PNL-RD-MECH | PAHU-04 (BMS Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 8 | 8 | 15 | 7 | 7 I/O points carried, 8C cable; length 15 m (typical_range:roofdeck_plant_area)
C0088 | BMS-PNL-RD-MECH | PAHU-04 (Equipment Supplier) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 15 | 5 | 5 I/O points carried, 6C cable; length 15 m (typical_range:roofdeck_plant_area)
C0089 | BMS-PNL-RD-MECH | PAHU-04 (ME Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0090 | BMS-PNL-RD-MECH | PAHU-05 (BMS Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 8 | 8 | 15 | 7 | 7 I/O points carried, 8C cable; length 15 m (typical_range:roofdeck_plant_area)
C0091 | BMS-PNL-RD-MECH | PAHU-05 (Equipment Supplier) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 15 | 5 | 5 I/O points carried, 6C cable; length 15 m (typical_range:roofdeck_plant_area)
C0092 | BMS-PNL-RD-MECH | PAHU-05 (ME Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0093 | BMS-PNL-RD-MECH | PAHU-06 (BMS Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 8 | 8 | 15 | 7 | 7 I/O points carried, 8C cable; length 15 m (typical_range:roofdeck_plant_area)
C0094 | BMS-PNL-RD-MECH | PAHU-06 (Equipment Supplier) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 15 | 5 | 5 I/O points carried, 6C cable; length 15 m (typical_range:roofdeck_plant_area)
C0095 | BMS-PNL-RD-MECH | PAHU-06 (ME Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0096 | BMS-PNL-RD-MECH | PAHU-07 (BMS Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 8 | 8 | 15 | 7 | 7 I/O points carried, 8C cable; length 15 m (typical_range:roofdeck_plant_area)
C0097 | BMS-PNL-RD-MECH | PAHU-07 (Equipment Supplier) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 6 | 6 | 15 | 5 | 5 I/O points carried, 6C cable; length 15 m (typical_range:roofdeck_plant_area)
C0098 | BMS-PNL-RD-MECH | PAHU-07 (ME Contractor) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0099 | BMS-PNL-LG-CHILLER | PCHWP-1 (BMS Contractor) | Primary CHW Pump | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0100 | BMS-PNL-LG-CHILLER | PCHWP-1 (Equipment Supplier) | Primary CHW Pump | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 5 | 6 | 12 | 5 | 5 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0101 | BMS-PNL-LG-CHILLER | PCHWP-2 (BMS Contractor) | Primary CHW Pump | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0102 | BMS-PNL-LG-CHILLER | PCHWP-2 (Equipment Supplier) | Primary CHW Pump | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 5 | 6 | 12 | 5 | 5 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0103 | BMS-PNL-LG-CHILLER | PCHWP-3 (BMS Contractor) | Primary CHW Pump | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0104 | BMS-PNL-LG-CHILLER | PCHWP-3 (Equipment Supplier) | Primary CHW Pump | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 5 | 6 | 12 | 5 | 5 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0105 | BMS-PNL-RD-MECH | RP-HZ-1 (Equipment Supplier) | Recirculating Pump | hot_water | Roof Deck HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0106 | BMS-PNL-RD-MECH | RP-HZ-2 (Equipment Supplier) | Recirculating Pump | hot_water | Roof Deck HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0107 | BMS-PNL-RD-MECH | RP-HZ-3 (Equipment Supplier) | Recirculating Pump | hot_water | Roof Deck HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0108 | BMS-PNL-LG-PLUMB | RP-LZ-1 (Equipment Supplier) | Recirculating Pump | hot_water | Lower Ground HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0109 | BMS-PNL-LG-PLUMB | RP-LZ-2 (Equipment Supplier) | Recirculating Pump | hot_water | Lower Ground HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0110 | BMS-PNL-LG-PLUMB | RP-LZ-3 (Equipment Supplier) | Recirculating Pump | hot_water | Lower Ground HW Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_same_room)
C0111 | BMS-PNL-LG-PLUMB | SB-1 (BMS Contractor) | Steam Boiler | steam | Lower Ground Laundry | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 9 | 12 | 12 | 8 | 8 I/O points carried, 12C cable; length 12 m (typical_range:plant_room_same_room)
C0112 | BMS-PNL-LG-PLUMB | SB-2 (BMS Contractor) | Steam Boiler | steam | Lower Ground Laundry | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 9 | 12 | 12 | 8 | 8 I/O points carried, 12C cable; length 12 m (typical_range:plant_room_same_room)
C0113 | BMS-PNL-GF | TEF-1.1 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Ground Floor Lobby | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0114 | BMS-PNL-GF | TEF-1.2 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Ground Floor Lobby | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0115 | BMS-PNL-GF | TEF-1.3 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Ground Floor Lobby | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0116 | BMS-PNL-GF | TEF-1.4 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Ground Floor Lobby | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0117 | BMS-PNL-2F-CASINO | TEF-2.1 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 2nd Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0118 | BMS-PNL-2F-CASINO | TEF-2.3 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 2nd Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0119 | BMS-PNL-2F-CASINO | TEF-2B.3 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 2nd Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0120 | BMS-PNL-3F | TEF-3A.1 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0121 | BMS-PNL-3F | TEF-3A.2 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0122 | BMS-PNL-3F | TEF-3B (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0123 | BMS-PNL-3F | TEF-3C.1 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0124 | BMS-PNL-3F | TEF-3C.2 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0125 | BMS-PNL-3F | TEF-3D.1 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0126 | BMS-PNL-3F | TEF-3D.10 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0127 | BMS-PNL-3F | TEF-3D.11 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0128 | BMS-PNL-3F | TEF-3D.12 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0129 | BMS-PNL-3F | TEF-3D.13 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0130 | BMS-PNL-3F | TEF-3D.14 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0131 | BMS-PNL-3F | TEF-3D.15 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0132 | BMS-PNL-3F | TEF-3D.16 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0133 | BMS-PNL-3F | TEF-3D.17 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0134 | BMS-PNL-3F | TEF-3D.18 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0135 | BMS-PNL-3F | TEF-3D.19 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0136 | BMS-PNL-3F | TEF-3D.2 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0137 | BMS-PNL-3F | TEF-3D.20 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0138 | BMS-PNL-3F | TEF-3D.3 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0139 | BMS-PNL-3F | TEF-3D.4 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0140 | BMS-PNL-3F | TEF-3D.5 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0141 | BMS-PNL-3F | TEF-3D.6 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0142 | BMS-PNL-3F | TEF-3D.7 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0143 | BMS-PNL-3F | TEF-3D.8 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0144 | BMS-PNL-3F | TEF-3D.9 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0145 | BMS-PNL-B1 | TEF-B.1 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0146 | BMS-PNL-B1 | TEF-B.10 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0147 | BMS-PNL-B1 | TEF-B.11 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0148 | BMS-PNL-B1 | TEF-B.12 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0149 | BMS-PNL-B1 | TEF-B.13 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0150 | BMS-PNL-B1 | TEF-B.14 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0151 | BMS-PNL-B1 | TEF-B.15 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0152 | BMS-PNL-B1 | TEF-B.16 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0153 | BMS-PNL-B1 | TEF-B.2 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0154 | BMS-PNL-B1 | TEF-B.3 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0155 | BMS-PNL-B1 | TEF-B.4 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0156 | BMS-PNL-B1 | TEF-B.5 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0157 | BMS-PNL-B1 | TEF-B.6 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0158 | BMS-PNL-B1 | TEF-B.7 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0159 | BMS-PNL-B1 | TEF-B.8 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0160 | BMS-PNL-B1 | TEF-B.9 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Basement 1 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 22 | 3 | 3 I/O points carried, 4C cable; length 22 m (typical_range:boh_same_floor)
C0161 | BMS-PNL-GF | TEF-GS.1 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Ground Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:guestroom_corridor)
C0162 | BMS-PNL-GF | TEF-GS.2 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Ground Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:guestroom_corridor)
C0163 | BMS-PNL-RD-MECH | TEF-RD.1 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Roof Deck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0164 | BMS-PNL-RD-MECH | TEF-RD.2 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Roof Deck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0165 | BMS-PNL-RD-MECH | TEF-RD.3 (Equipment Supplier) | Exhaust Fan (Toilet) | ventilation | Roof Deck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:roofdeck_plant_area)
C0166 | BMS-PNL-LG-CHILLER | CH-1 (Network) | Chiller (Package Water-Cooled) | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0167 | BMS-PNL-LG-CHILLER | CH-2 (Network) | Chiller (Package Water-Cooled) | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0168 | BMS-PNL-LG-CHILLER | CH-3 (Network) | Chiller (Package Water-Cooled) | chilled_water | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0169 | BMS-PNL-LG-CHILLER | BTU-1 (Network) | BTU Meter | btu_metering | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0170 | BMS-PNL-LG-CHILLER | BTU-2 (Network) | BTU Meter | btu_metering | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0171 | BMS-PNL-LG-CHILLER | BTU-3 (Network) | BTU Meter | btu_metering | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0172 | BMS-PNL-LG-CHILLER | BTU-4 (Network) | BTU Meter | btu_metering | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0173 | BMS-PNL-LG-CHILLER | BTU-5 (Network) | BTU Meter | btu_metering | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0174 | BMS-PNL-RD-MECH | DOAS-RD1 (Network) | DOAS Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:roofdeck_plant_area)
C0175 | BMS-PNL-RD-MECH | DOAS-RD2 (Network) | DOAS Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:roofdeck_plant_area)
C0176 | BMS-PNL-2F-CASINO | DOAS-2F-CASINO (Network) | DOAS Unit | ventilation | 2nd Floor Casino MVAC Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 22 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 22 m (typical_range:boh_same_floor)
C0177 | BMS-PNL-RD-MECH | PAHU-01 (Network) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:roofdeck_plant_area)
C0178 | BMS-PNL-RD-MECH | PAHU-02 (Network) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:roofdeck_plant_area)
C0179 | BMS-PNL-RD-MECH | PAHU-03 (Network) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:roofdeck_plant_area)
C0180 | BMS-PNL-RD-MECH | PAHU-04 (Network) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:roofdeck_plant_area)
C0181 | BMS-PNL-RD-MECH | PAHU-05 (Network) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:roofdeck_plant_area)
C0182 | BMS-PNL-RD-MECH | PAHU-06 (Network) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:roofdeck_plant_area)
C0183 | BMS-PNL-RD-MECH | PAHU-07 (Network) | Precooled Air Handling Unit | ventilation | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:roofdeck_plant_area)
C0184 | BMS-PNL-GF | PM-MAIN (Network) | Multifunction Power Meter (Main) | power_metering | Main Switchgear Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0185 | BMS-PNL-LG-CHILLER | PM-CHILLER-1 (Network) | Multifunction Power Meter (Feeder) | power_metering | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0186 | BMS-PNL-LG-CHILLER | PM-CHILLER-2 (Network) | Multifunction Power Meter (Feeder) | power_metering | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0187 | BMS-PNL-LG-CHILLER | PM-CHILLER-3 (Network) | Multifunction Power Meter (Feeder) | power_metering | 2nd Level Mechanical Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0188 | BMS-PNL-2F-CASINO | PM-CASINO-FB (Network) | Multifunction Power Meter (Feeder) | power_metering | 2nd Floor Casino | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 22 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 22 m (typical_range:boh_same_floor)
C0189 | BMS-PNL-2F-CASINO | PM-KITCHEN-2F (Network) | Multifunction Power Meter (Feeder) | power_metering | 2nd Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 22 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 22 m (typical_range:boh_same_floor)
C0190 | BMS-PNL-GF | PM-LOBBY-GF (Network) | Multifunction Power Meter (Feeder) | power_metering | Ground Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 35 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 35 m (typical_range:guestroom_corridor)
C0191 | BMS-PNL-GF | PM-ELEVATOR (Network) | Multifunction Power Meter (Feeder) | power_metering | Ground Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 35 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 35 m (typical_range:guestroom_corridor)
C0192 | BMS-PNL-3F | PM-LIGHTING-GUEST (Network) | Multifunction Power Meter (Feeder) | power_metering | 3rd Floor Amenity | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 22 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 22 m (typical_range:boh_same_floor)
C0193 | BMS-PNL-LG-PLUMB | PM-LAUNDRY-LG (Network) | Multifunction Power Meter (Feeder) | power_metering | Lower Ground Laundry | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_same_room)
C0194 | BMS-PNL-RD-MECH | PM-ROOFDECK-MECH (Network) | Multifunction Power Meter (Feeder) | power_metering | Roof Deck Mechanical | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:roofdeck_plant_area)

## Trunks
ID | From | To | Cable Type | Length (m) | Notes
T0195 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for 2nd Floor — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0196 | BMS Server Room (head-end) | All BMS panels at 3rd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for 3rd Floor — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0197 | BMS Server Room (head-end) | All BMS panels at Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Basement — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0198 | BMS Server Room (head-end) | All BMS panels at Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Ground — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0199 | BMS Server Room (head-end) | All BMS panels at Lower Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Lower Ground — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0200 | BMS Server Room (head-end) | BMS panel controllers (per topology id ?) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 380 | Backbone per agent's trunk_topology entry ?
T0201 | BMS Server Room (head-end) | BMS panel controllers (per topology id ?) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 700 | Backbone per agent's trunk_topology entry ?

## Panel Power Feeds
ID | From | To | Cable Type | Length (m) | Notes
P0202 | Local panelboard / EE-supplied feeder | BMS-PNL-2F-CASINO — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed)
P0203 | Local panelboard / EE-supplied feeder | BMS-PNL-3F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed)
P0204 | Local panelboard / EE-supplied feeder | BMS-PNL-B1 — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed)
P0205 | Local panelboard / EE-supplied feeder | BMS-PNL-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed)
P0206 | Local panelboard / EE-supplied feeder | BMS-PNL-LG-CHILLER — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed)
P0207 | Local panelboard / EE-supplied feeder | BMS-PNL-LG-PLUMB — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed)
P0208 | Local panelboard / EE-supplied feeder | BMS-PNL-RD-CT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed)
P0209 | Local panelboard / EE-supplied feeder | BMS-PNL-RD-MECH — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:panel_power_feed)