## Summary
A4 — Panel Schedule Summary
Total panels | 8
Total physical I/O | 622
Total HLI subpoints | 102
Total network drops | 29
Total I/O points | 753
Estimated total controllers | 19
Estimated total power (W) | 620

## Panel Schedule
Panel | Location | System Scope | Equipment Count | Physical I/O | HLI Subpoints | Network Drops | Total I/O | DDC Controllers | Network Gateway | Total Controllers | Power (W) | Enclosure
BMS-PNL-2F-CASINO | 2nd Floor BOH / 2nd Floor Casino / 2nd Floor Casino MVAC Room | casino_mvac, common_area, power_metering, ventilation | 11 | 84 | 4 | 3 | 91 | 3 | 1 | 3 | 90 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-3F | 3rd Floor Amenity | power_metering, ventilation | 26 | 75 | 0 | 1 | 76 | 2 | 1 | 2 | 55 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-B1 | Basement 1 / Basement 1 BOH | common_area, ventilation | 17 | 63 | 1 | 0 | 64 | 2 | 0 | 2 | 50 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-GF | Ground Floor / Ground Floor BOH / Ground Floor Lobby / Ground Floor Mezzanine BOH / Main Switchgear Room | common_area, power_metering, ventilation | 16 | 63 | 2 | 3 | 68 | 2 | 1 | 2 | 65 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-LG-CHILLER | 2nd Level Mechanical Room | btu_metering, chilled_water, power_metering | 20 | 72 | 60 | 11 | 143 | 2 | 1 | 2 | 105 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-LG-PLUMB | Lower Ground HW Plant / Lower Ground Laundry | hot_water, power_metering, steam | 13 | 40 | 26 | 1 | 67 | 1 | 1 | 2 | 55 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-RD-CT | Roof Deck Mechanical | condenser_water | 4 | 40 | 0 | 0 | 40 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-RD-MECH | Roof Deck / Roof Deck HW Plant / Roof Deck Mechanical | hot_water, power_metering, ventilation | 25 | 185 | 9 | 10 | 204 | 5 | 1 | 5 | 175 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare

## Equipment per Panel
Panel | Equipment Instance
BMS-PNL-2F-CASINO | AHU-2F-1
BMS-PNL-2F-CASINO | AHU-2M.1
BMS-PNL-2F-CASINO | AHU-2M.2
BMS-PNL-2F-CASINO | DOAS-2F-CASINO
BMS-PNL-2F-CASINO | ION-2F-1
BMS-PNL-2F-CASINO | ION-2F-2
BMS-PNL-2F-CASINO | PM-CASINO-FB
BMS-PNL-2F-CASINO | PM-KITCHEN-2F
BMS-PNL-2F-CASINO | TEF-2.1
BMS-PNL-2F-CASINO | TEF-2.3
BMS-PNL-2F-CASINO | TEF-2B.3
BMS-PNL-3F | PM-LIGHTING-GUEST
BMS-PNL-3F | TEF-3A.1
BMS-PNL-3F | TEF-3A.2
BMS-PNL-3F | TEF-3B
BMS-PNL-3F | TEF-3C.1
BMS-PNL-3F | TEF-3C.2
BMS-PNL-3F | TEF-3D.1
BMS-PNL-3F | TEF-3D.10
BMS-PNL-3F | TEF-3D.11
BMS-PNL-3F | TEF-3D.12
BMS-PNL-3F | TEF-3D.13
BMS-PNL-3F | TEF-3D.14
BMS-PNL-3F | TEF-3D.15
BMS-PNL-3F | TEF-3D.16
BMS-PNL-3F | TEF-3D.17
BMS-PNL-3F | TEF-3D.18
BMS-PNL-3F | TEF-3D.19
BMS-PNL-3F | TEF-3D.2
BMS-PNL-3F | TEF-3D.20
BMS-PNL-3F | TEF-3D.3
BMS-PNL-3F | TEF-3D.4
BMS-PNL-3F | TEF-3D.5
BMS-PNL-3F | TEF-3D.6
BMS-PNL-3F | TEF-3D.7
BMS-PNL-3F | TEF-3D.8
BMS-PNL-3F | TEF-3D.9
BMS-PNL-B1 | AHU-B1-1
BMS-PNL-B1 | TEF-B.1
BMS-PNL-B1 | TEF-B.10
BMS-PNL-B1 | TEF-B.11
BMS-PNL-B1 | TEF-B.12
BMS-PNL-B1 | TEF-B.13
BMS-PNL-B1 | TEF-B.14
BMS-PNL-B1 | TEF-B.15
BMS-PNL-B1 | TEF-B.16
BMS-PNL-B1 | TEF-B.2
BMS-PNL-B1 | TEF-B.3
BMS-PNL-B1 | TEF-B.4
BMS-PNL-B1 | TEF-B.5
BMS-PNL-B1 | TEF-B.6
BMS-PNL-B1 | TEF-B.7
BMS-PNL-B1 | TEF-B.8
BMS-PNL-B1 | TEF-B.9
BMS-PNL-GF | AHU-GF-1
BMS-PNL-GF | AHU-GFM-1
BMS-PNL-GF | EF-1.2A
BMS-PNL-GF | EF-1MR.1
BMS-PNL-GF | EF-1STO.1
BMS-PNL-GF | EF-LPG.1
BMS-PNL-GF | EF-MRF.1
BMS-PNL-GF | PM-ELEVATOR
BMS-PNL-GF | PM-LOBBY-GF
BMS-PNL-GF | PM-MAIN
BMS-PNL-GF | TEF-1.1
BMS-PNL-GF | TEF-1.2
BMS-PNL-GF | TEF-1.3
BMS-PNL-GF | TEF-1.4
BMS-PNL-GF | TEF-GS.1
BMS-PNL-GF | TEF-GS.2
BMS-PNL-LG-CHILLER | BTU-1
BMS-PNL-LG-CHILLER | BTU-2
BMS-PNL-LG-CHILLER | BTU-3
BMS-PNL-LG-CHILLER | BTU-4
BMS-PNL-LG-CHILLER | BTU-5
BMS-PNL-LG-CHILLER | CH-1
BMS-PNL-LG-CHILLER | CH-2
BMS-PNL-LG-CHILLER | CH-3
BMS-PNL-LG-CHILLER | CHW-BYPASS
BMS-PNL-LG-CHILLER | CHW-HDR-R
BMS-PNL-LG-CHILLER | CHW-HDR-S
BMS-PNL-LG-CHILLER | CWP-1
BMS-PNL-LG-CHILLER | CWP-2
BMS-PNL-LG-CHILLER | CWP-3
BMS-PNL-LG-CHILLER | PCHWP-1
BMS-PNL-LG-CHILLER | PCHWP-2
BMS-PNL-LG-CHILLER | PCHWP-3
BMS-PNL-LG-CHILLER | PM-CHILLER-1
BMS-PNL-LG-CHILLER | PM-CHILLER-2
BMS-PNL-LG-CHILLER | PM-CHILLER-3
BMS-PNL-LG-PLUMB | HP-LZ-1
BMS-PNL-LG-PLUMB | HP-LZ-2
BMS-PNL-LG-PLUMB | HP-LZ-3
BMS-PNL-LG-PLUMB | HW-HEADERS
BMS-PNL-LG-PLUMB | HWT-LZ-1
BMS-PNL-LG-PLUMB | HWT-LZ-2
BMS-PNL-LG-PLUMB | HWT-LZ-3
BMS-PNL-LG-PLUMB | PM-LAUNDRY-LG
BMS-PNL-LG-PLUMB | RP-LZ-1
BMS-PNL-LG-PLUMB | RP-LZ-2
BMS-PNL-LG-PLUMB | RP-LZ-3
BMS-PNL-LG-PLUMB | SB-1
BMS-PNL-LG-PLUMB | SB-2
BMS-PNL-RD-CT | CT-1
BMS-PNL-RD-CT | CT-2
BMS-PNL-RD-CT | CT-3
BMS-PNL-RD-CT | CT-COMMON
BMS-PNL-RD-MECH | DOAS-RD1
BMS-PNL-RD-MECH | DOAS-RD2
BMS-PNL-RD-MECH | EF-1
BMS-PNL-RD-MECH | EF-RD.1
BMS-PNL-RD-MECH | EF-RD.2
BMS-PNL-RD-MECH | HP-HZ-1
BMS-PNL-RD-MECH | HP-HZ-2
BMS-PNL-RD-MECH | HP-HZ-3
BMS-PNL-RD-MECH | HWT-HZ-1
BMS-PNL-RD-MECH | HWT-HZ-2
BMS-PNL-RD-MECH | HWT-HZ-3
BMS-PNL-RD-MECH | PAHU-01
BMS-PNL-RD-MECH | PAHU-02
BMS-PNL-RD-MECH | PAHU-03
BMS-PNL-RD-MECH | PAHU-04
BMS-PNL-RD-MECH | PAHU-05
BMS-PNL-RD-MECH | PAHU-06
BMS-PNL-RD-MECH | PAHU-07
BMS-PNL-RD-MECH | PM-ROOFDECK-MECH
BMS-PNL-RD-MECH | RP-HZ-1
BMS-PNL-RD-MECH | RP-HZ-2
BMS-PNL-RD-MECH | RP-HZ-3
BMS-PNL-RD-MECH | TEF-RD.1
BMS-PNL-RD-MECH | TEF-RD.2
BMS-PNL-RD-MECH | TEF-RD.3