Table of Contents

# 08 — Customer Clarifications (RFI list)

Project: Kingsford Hotel Bacolod — BMS Date: 2026-04-28

Items requiring Megaworld input. Each Q-NNN has the question, why we need it, our current assumption (with A-NNN cross-ref), and the impact of the customer’s answer.

## Q-001 — Confirm project stage: Greenfield (new construction) per drawing evidence, vs. cover-letter “Rehabilitation” wording

- Why: Cover letter uses rehabilitation; Construction Bulletin No.8 (2025-11) and absence of existing-system inventory point to greenfield. We have classified greenfield (D-002 / A-001).

- Customer to confirm: Project is greenfield new construction.

- Impact: ±30% on proposal scope (demolition, hot cutover, after-hours premiums)

## Q-002 — Confirm plumbing scope coverage

- Why: PL points list provided covers Centralized Hot Water only. Domestic water booster pumps, transfer pumps, sump pumps, sewage ejectors, water tanks are not in the package.

- Customer to provide: Remaining tabs of source workbook (DRC-004-2024) for plumbing equipment beyond hot water; OR confirm that hot water alone is the BMS plumbing scope.

- Current assumption: A-011 — hot water only.

- Impact: Adds ~30 DI/DO, ~20 cables, ~PHP 600k–1M if domestic-water + sump scope added

## Q-003 — Guestroom per-room HVAC controls in BMS scope?

- Why: Guestroom-floor BMS points show only DOAS/PAHU/corridor exhausts; no per-room FCU thermostat enumeration.

- Customer to confirm: Per-room FCU controllers + thermostats for ~280 guestrooms (12 floors × ~24 rooms) are in BMS contractor scope, OR under fit-out / equipment-supplier scope.

- Current assumption: A-008 — out of BMS scope.

- Impact: PHP 8–14M if in scope

## Q-004 — Required completion date / project schedule

- Why: Drives mobilization, manpower loading, T&C windows.

- Customer to provide: Required handover date or contract-execution-to-handover duration.

- Current assumption: A-003 — 16 weeks

- Impact: Crash schedule adds night-shift + duplicate teams; relaxed schedule reduces peak manpower and idle time

## Q-005 — Architectural floor plans + mechanical/plumbing layout drawings

- Why: Enable full cable-route measurement; the EE/ECE sheets carry architectural backgrounds but mechanical/plumbing equipment locations are not depicted.

- Customer to provide: AR floor plans (all floors), ME layouts (chiller plant, roofdeck mechanical, AHU rooms), PL layouts.

- Current assumption: A-012 — typical-range cable lengths per context per Op#11 reasoned table.

- Impact: Refines BOQ cable + conduit ±15%

## Q-006 — Server-room / head-end PC location

- Why: Drives fiber backbone length and 24V/UPS routing.

- Current assumption: A-006 — Lower Ground IT/telecom room.

- Impact: Alternate location adds ~30 m fiber + minor

## Q-007 — Hotel PMS (Property Management System) integration scope

- Why: Determines whether per-room HVAC setbacks driven by check-in/check-out events are in scope.

- Current assumption: A-007 — out of base scope, offered as option.

- Impact: PHP 800k–1.5M if added (gateway + per-room mapping)

## Q-008 — Casino-floor CO sensors at AHU/DOAS return air

- Why: Casino + back-of-house return-air mixing typically requires CO monitoring per gaming-board / IAQ minimums; not explicitly enumerated in ME points list.

- Current assumption: A-009 — 1 CO sensor per casino-serving AHU/DOAS return (3 total).

- Impact: Saves PHP 200k if removed; or expands if regulator demands more

## Q-009 — Complete EE drawing set (full EE-01..EE-24 + EE-24 part 2)

- Why: EE Plan PDF provided is Construction Bulletin No.8 only — covers revised sheets EE-03/06/09/12/21/22/23/24-part-1. Other unrevised sheets needed for full panel-context.

- Customer to provide: Complete EE set, all currently-issued revisions; EE-24 part 2 power riser.

- Current assumption: Use load schedules EE-21..23 + riser EE-24 part 1 as proxy.

- Impact: Refines per-panel power-feed sourcing; minor BOQ effect (≤2%)

## Q-010 — BMS-04 sheet

- Why: BMS-03 P&ID detail bubbles reference BMS-04 (“1/BMS-04”) but the sheet is not in the PDF.

- Customer to provide: BMS-04 sheet content.

- Impact: Likely minor; could clarify casino-MVAC or boiler details

## Q-011 — PPCAS-14 panel relocation

- Why: EE-09 carries an open APD markup: “Relocate this provision PPCAS-14 inside the casino lobby. IMPLEMENT OR NOT?”

- Customer to confirm: Implement relocation or retain original PPCAS-14 location.

- Impact: ~5–8 m of trunk cable + ~PHP 30k

## Q-012 — Brand approvals for BMS, head-end PCs, and balance-of-plant equipment

- Why: Megaworld customer-kb approved-brands list is STUB; awaiting MC Standards Section 9 firm-up.

- Customer to confirm: Siemens (BMS DDC + head-end), Dell (server + workstation), open-tier-1 for VFDs/UPS/network — or substitutes.

- Current assumption: A-002 — Siemens + Dell defaults.

- Impact: ±5–8% material BOQ swing

## Q-013 — Working hours / site-access constraints

- Why: Daytime vs. night vs. shift-restricted affects labor productivity.

- Current assumption: A-004 — daytime, no shift restrictions.

- Impact: ~25% labor premium if night work mandated

## Q-014 — Commercial terms: currency, payment, warranty, retention, taxes

- Why: Cover letter is silent on commercial terms.

- Current assumption: A-005 — PHP, 30-day, 12-month warranty, 10% retention, 12% VAT.

- Impact: Retention swing affects working capital; longer warranty affects spare-parts cost

## Q-015 — ECE-05 (likely GF Aux) and ECE-06 (likely 2F FDAS) sheets

- Why: Sheets are present in the index but not in the PDF; coordination with Aux/FDAS routing typically shares BMS shaft space.

- Customer to provide: ECE-05, ECE-06.

- Impact: Minor — coordination only

## Q-016 — 1-year preventive maintenance scope (option)

- Why: Standard option for hospitality projects.

- Customer to confirm: Include in base proposal or separate option line.

- Current assumption: Offered as option (A-033 covers training only)

## Q-017 — FAT location and witness participation

- Why: Drives logistics + customer-rep mobilization

- Current assumption: A-034 — Manila workshop, 2 days, customer witness invited

- Impact: Off-Manila FAT adds travel cost