## Summary
A3 — Cable Schedule, Audit View
Project | Kingsford Hotel Bacolod — BMS
Canonical source | A3-cable-schedule.yaml
How to record corrections | Edit the canonical YAML directly — add a verification: block to the affected row(s)
Totals
Total cables | 44
Total length (m) | 1,107
Field cables | 29
Trunk cables | 2
Panel power feeds | 13
Verification status
Status | Count | % of total
verified | 0 | 0%
needs_correction | 0 | 0%
uncertain | 0 | 0%
unverified | 44 | 100%
⚠ Known weak points
Cable lengths are estimates based on assumption A-001 (30 m average panel-to-device run, 80 m trunk per floor). Field-verified lengths typically vary by ±20% per cable. THIS IS THE SYSTEM'S WEAKEST AUTO-GENERATED QUANTITY — please verify before issuing the BOQ to the customer.
How corrections flow
1. Open A3-cable-schedule.yaml in any text editor.
2. Find the affected row by ID (column A in the Detail sheet).
3. Add a verification: block — see the 'Verification schema' sheet for the template.
4. Re-run: python3 _playbook/tools/generate-deliverables.py <project>
5. Corrections flow through B4 manhours, BOQ material costs, and final deliverables automatically.

## By Panel
Panel | Cable count | Total length (m)
BMS-PNL-CASINO-2F | 3 | 78
BMS-PNL-AHU-RD | 4 | 56
BMS-PNL-CHWPLANT-2F | 5 | 56
BMS-PNL-PLUMBING-LG | 3 | 36
BMS-PNL-VENT-GF | 1 | 35
BMS-PNL-VENT-2F | 1 | 35
BMS-PNL-VENT-3F | 1 | 35
BMS-PNL-CT-RD | 2 | 34
BMS-PNL-BOHAHU-2F | 2 | 24
BMS-PNL-PLUMBING-RD | 2 | 24
BMS-PNL-AHU-2F | 2 | 24
BMS-PNL-BOILER-LG | 2 | 22
BMS-PNL-VENT-RD | 1 | 14
TOTAL (field cables) | 29 | 473

## By Floor
Floor | Cable count | Total length (m)
2nd Floor | 13 | 217
RD | 9 | 128
LG | 5 | 58
GF | 1 | 35
3F | 1 | 35
TOTAL | 29 | 473

## By Cable Type
Cable type | Count | Total length (m)
4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 17 | 305
4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 12 | 168

## Detail (cables)
ID | From | To | Cable type | Length (m) | Status | Corrected (m) | Verified by | Date | Drawing ref | Notes
C0001 | BMS-PNL-BOHAHU-2F | AHU-2/B.2/B.3/PP/CL/FRE/FRD (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 12 | unverified
C0002 | BMS-PNL-BOHAHU-2F | AHU-2/B.2/B.3/PP/CL/FRE/FRD (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 12 | unverified
C0003 | BMS-PNL-AHU-RD | AHU-RD (with CHW mod valve) (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 16 | unverified
C0004 | BMS-PNL-AHU-RD | AHU-RD (with CHW mod valve) (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 14 | unverified
C0005 | BMS-PNL-CHWPLANT-2F | CDWP-1 to CDWP-3 (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 12 | unverified
C0006 | BMS-PNL-CHWPLANT-2F | CH-1 to CH-3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 14 | unverified
C0007 | BMS-PNL-CHWPLANT-2F | CH-1 to CH-3 (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 12 | unverified
C0008 | BMS-PNL-CHWPLANT-2F | CHW Supply & Return Main Header (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 8 | unverified
C0009 | BMS-PNL-CHWPLANT-2F | CHWP-1 to CHWP-3 (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 10 | unverified
C0010 | BMS-PNL-CT-RD | CT-1 to CT-3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 18 | unverified
C0011 | BMS-PNL-CT-RD | CT-1 to CT-3 (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 16 | unverified
C0012 | BMS-PNL-CASINO-2F | DOAS (Casino) — 2 units (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 26 | unverified
C0013 | BMS-PNL-CASINO-2F | DOAS (Casino) — 2 units (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 24 | unverified
C0014 | BMS-PNL-VENT-RD | EF-RD.1/RD.2, EF-1 (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 14 | unverified
C0015 | BMS-PNL-PLUMBING-LG | HW Supply & Return Header (LG) (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 10 | unverified
C0016 | BMS-PNL-PLUMBING-RD | HWT-HZ (×3) (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 12 | unverified
C0017 | BMS-PNL-PLUMBING-LG | HWT-LZ (×3) (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 14 | unverified
C0018 | BMS-PNL-AHU-2F | PAHU-0.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 12 | unverified
C0019 | BMS-PNL-AHU-2F | PAHU-0.1 (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 12 | unverified
C0020 | BMS-PNL-AHU-RD | PAHU-RD (×2) (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 14 | unverified
C0021 | BMS-PNL-AHU-RD | PAHU-RD (×2) (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 12 | unverified
C0022 | BMS-PNL-PLUMBING-RD | RP-HZ (×3) (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 12 | unverified
C0023 | BMS-PNL-PLUMBING-LG | RP-LZ (×3) (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 12 | unverified
C0024 | BMS-PNL-BOILER-LG | SB-1 & SB-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 12 | unverified
C0025 | BMS-PNL-BOILER-LG | SB-1 & SB-2 (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 10 | unverified
C0026 | BMS-PNL-CASINO-2F | Sanitizer for AHU-2M.1/2M.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 28 | unverified
C0027 | BMS-PNL-VENT-GF | TEF-1.1 to 1.4 + EF-1.2A/LPG.1/1MR.1/1STO.1/MRF.1 (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 35 | unverified
C0028 | BMS-PNL-VENT-2F | TEF-2.1/2.3/2B.3 + EF-2B.1/2B.2/GS.1&GS.2 + EF-2.1 to 2.4 + EF-CHRx2 (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 35 | unverified
C0029 | BMS-PNL-VENT-3F | TEF-3Ax2/3B/3Cx2/3Dx20 + others (ME Contractor) | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 35 | unverified
T0030 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0031 | BMS Server Room (head-end) | BMS panel controllers (per topology id mstp_main_backbone) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 320 | unverified
P0032 | Local panelboard / EE-supplied feeder | BMS-PNL-AHU-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0033 | Local panelboard / EE-supplied feeder | BMS-PNL-AHU-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0034 | Local panelboard / EE-supplied feeder | BMS-PNL-BOHAHU-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0035 | Local panelboard / EE-supplied feeder | BMS-PNL-BOILER-LG — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0036 | Local panelboard / EE-supplied feeder | BMS-PNL-CASINO-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0037 | Local panelboard / EE-supplied feeder | BMS-PNL-CHWPLANT-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0038 | Local panelboard / EE-supplied feeder | BMS-PNL-CT-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0039 | Local panelboard / EE-supplied feeder | BMS-PNL-PLUMBING-LG — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0040 | Local panelboard / EE-supplied feeder | BMS-PNL-PLUMBING-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0041 | Local panelboard / EE-supplied feeder | BMS-PNL-VENT-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0042 | Local panelboard / EE-supplied feeder | BMS-PNL-VENT-3F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0043 | Local panelboard / EE-supplied feeder | BMS-PNL-VENT-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified
P0044 | Local panelboard / EE-supplied feeder | BMS-PNL-VENT-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | unverified

## Verification schema
How to record verification / corrections in A3-cable-schedule.yaml
Find the affected row in the YAML by ID (Detail sheet column A) and add a verification: block:
- id: C0001
from: PNL-CH-PLANT-GND
to: CH-1 (BMS Contractor)
cable_type: 4C × 1.5 mm² shielded FRLS
length_m: 30
verification: # ADDED by team
status: needs_correction # unverified ¦ verified ¦ needs_correction ¦ uncertain
corrected_length_m: 42 # team's measured / confirmed value
verified_by: J. Cruz
verified_date: 2026-05-10
drawing_ref: "EE-09 grid B-2"
notes: ""
After saving, re-run: python3 _playbook/tools/generate-deliverables.py <project>
Corrections propagate to B4 manhours, BOQ, and final deliverables automatically.
Recommended verification methods (priority order):
1. Site walkthrough with measurement (most accurate; for cable lengths, after structural completion).
2. Properly-scaled architectural drawings.
3. Mechanical contractor's tray layout combined with BMS panel locations.
4. A-001 default with ±20% contingency in BOQ — last resort.