## Summary
A2 — Equipment Takeoff Summary
Total instances | 23
By equipment class
Exhaust Fan (General) | 4
AHU (Chilled-Water-Served) | 2
CHW Supply Main Header | 2
Heat Pump | 2
Calorifier (Hot Water Storage Tank) | 2
Precooled Air Handling Unit | 2
Recirculating Pump | 2
Condenser Water Pump | 1
Chiller (Package Water-Cooled) | 1
Primary CHW Pump | 1
Cooling Tower | 1
DOAS Unit | 1
Steam Boiler | 1
Ozone Generator (UV-light or Corona) | 1
By location
2F | 9
RD | 7
LG | 5
GF | 1
3F | 1
By panel
BMS-PNL-CHWPLANT-2F | 4
BMS-PNL-PLUMBING-LG | 4
BMS-PNL-PLUMBING-RD | 3
BMS-PNL-AHU-RD | 2
BMS-PNL-CASINO-2F | 2
BMS-PNL-BOHAHU-2F | 1
BMS-PNL-CT-RD | 1
BMS-PNL-VENT-RD | 1
BMS-PNL-AHU-2F | 1
BMS-PNL-BOILER-LG | 1
BMS-PNL-VENT-GF | 1
BMS-PNL-VENT-2F | 1
BMS-PNL-VENT-3F | 1

## Equipment Takeoff
ID | Equipment Class | Quantity | Location | System | Panel | Primary C/O | Physical I/O | HLI Subpoints | Network Drops | Total I/O | Make/Model Assumed | Network Type | Typical Supplier | Notes
AHU-2/B.2/B.3/PP/CL/FRE/FRD | AHU (Chilled-Water-Served) | 1 | 2F | Air Handling — Basement / Podium BOH | BMS-PNL-BOHAHU-2F | BMS Contractor | 120 | 20 | 0 | 140 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-RD (with CHW mod valve) | AHU (Chilled-Water-Served) | 1 | RD | Air Handling — Roofdeck AHU | BMS-PNL-AHU-RD | BMS Contractor | 32 | 0 | 0 | 32 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
CDWP-1 to CDWP-3 | Condenser Water Pump | 1 | 2F | Chilled Water Plant | BMS-PNL-CHWPLANT-2F | ME Contractor | 12 | 0 | 0 | 12 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
CH-1 to CH-3 | Chiller (Package Water-Cooled) | 1 | 2F | Chilled Water Plant | BMS-PNL-CHWPLANT-2F | ME Contractor | 81 | 0 | 0 | 81 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CHW Supply & Return Main Header | CHW Supply Main Header | 1 | 2F | Chilled Water Plant | BMS-PNL-CHWPLANT-2F | BMS Contractor | 7 | 0 | 0 | 7 | BMS T+P sensors on CHW supply manifold | Hardwired | BMS contractor | Field instrumentation only.
CHWP-1 to CHWP-3 | Primary CHW Pump | 1 | 2F | Chilled Water Plant | BMS-PNL-CHWPLANT-2F | ME Contractor | 21 | 0 | 0 | 21 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
CT-1 to CT-3 | Cooling Tower | 1 | RD | Heat Rejection — Cooling Tower | BMS-PNL-CT-RD | BMS Contractor | 35 | 1 | 0 | 36 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
DOAS (Casino) — 2 units | DOAS Unit | 1 | 2F | Casino MVAC — Dedicated Outdoor Air | BMS-PNL-CASINO-2F | BMS Contractor | 26 | 4 | 0 | 30 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
EF-RD.1/RD.2, EF-1 | Exhaust Fan (General) | 1 | RD | General Ventilation | BMS-PNL-VENT-RD | ME Contractor | 9 | 0 | 0 | 9 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
HP-HZ (×3) | Heat Pump | 1 | RD | Plumbing — Sanitary Hot Water | BMS-PNL-PLUMBING-RD | Equipment Supplier | 0 | 9 | 0 | 9 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-LZ (×3) | Heat Pump | 1 | LG | Plumbing — Sanitary Hot Water | BMS-PNL-PLUMBING-LG | Equipment Supplier | 0 | 9 | 0 | 9 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HW Supply & Return Header (LG) | CHW Supply Main Header | 1 | LG | Plumbing — Sanitary Hot Water | BMS-PNL-PLUMBING-LG | BMS Contractor | 6 | 0 | 0 | 6 | BMS T+P sensors on CHW supply manifold | Hardwired | BMS contractor | Field instrumentation only.
HWT-HZ (×3) | Calorifier (Hot Water Storage Tank) | 1 | RD | Plumbing — Sanitary Hot Water | BMS-PNL-PLUMBING-RD | BMS Contractor | 3 | 0 | 0 | 3 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-LZ (×3) | Calorifier (Hot Water Storage Tank) | 1 | LG | Plumbing — Sanitary Hot Water | BMS-PNL-PLUMBING-LG | BMS Contractor | 3 | 0 | 0 | 3 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
PAHU-0.1 | Precooled Air Handling Unit | 1 | 2F | Air Handling — Pre-cooled | BMS-PNL-AHU-2F | BMS Contractor | 12 | 4 | 0 | 16 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-RD (×2) | Precooled Air Handling Unit | 1 | RD | Air Handling — Pre-cooled (Roofdeck) | BMS-PNL-AHU-RD | ME Contractor | 12 | 2 | 0 | 14 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
RP-HZ (×3) | Recirculating Pump | 1 | RD | Plumbing — Sanitary Hot Water | BMS-PNL-PLUMBING-RD | ME Contractor | 9 | 0 | 0 | 9 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-LZ (×3) | Recirculating Pump | 1 | LG | Plumbing — Sanitary Hot Water | BMS-PNL-PLUMBING-LG | ME Contractor | 9 | 0 | 0 | 9 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
SB-1 & SB-2 | Steam Boiler | 1 | LG | Boiler / Laundry | BMS-PNL-BOILER-LG | ME Contractor | 22 | 0 | 0 | 22 | Fire-tube steam boiler with multi-stage burner, fuel-oil fired (typical for hotel laundry) | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies steam pressure, feedwater T, fluegas T+O2 sensors. Boiler equipment provides aux contacts for status/HOA/trip points.
Sanitizer for AHU-2M.1/2M.2 | Ozone Generator (UV-light or Corona) | 1 | 2F | Casino MVAC — Smoke Sanitizer | BMS-PNL-CASINO-2F | Equipment Supplier | 4 | 0 | 0 | 4 | UV-light or corona-discharge ozone generator (paired with Casino AHU) | Hardwired | Equipment supplier | Casino-specific air-treatment device. BMS monitors status/trip and reads VOC sensor (BMS-supplied).
TEF-1.1 to 1.4 + EF-1.2A/LPG.1/1MR.1/1STO.1/MRF.1 | Exhaust Fan (General) | 1 | GF | General Ventilation | BMS-PNL-VENT-GF | ME Contractor | 27 | 0 | 0 | 27 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2.1/2.3/2B.3 + EF-2B.1/2B.2/GS.1&GS.2 + EF-2.1 to 2.4 + EF-CHRx2 | Exhaust Fan (General) | 1 | 2F | General Ventilation | BMS-PNL-VENT-2F | ME Contractor | 39 | 0 | 0 | 39 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3Ax2/3B/3Cx2/3Dx20 + others | Exhaust Fan (General) | 1 | 3F | General Ventilation | BMS-PNL-VENT-3F | ME Contractor | 81 | 0 | 0 | 81 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.