## Summary
A3 — Cable Schedule Summary
Total field cable runs | 29
Total field cable length (m) | 473
Total trunk cable length (m) | 400
Total power feed length (m) | 234
GRAND TOTAL cable length (m) | 1107
By cable type (m)
4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 305
4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 168

## Field Cables
ID | From | To | Equipment Class | System | Location | Cable Type | Conductors Required | Conductors Specified | Length (m) | I/O Points Carried | Notes
C0001 | BMS-PNL-BOHAHU-2F | AHU-2/B.2/B.3/PP/CL/FRE/FRD (BMS Contractor) | AHU (Chilled-Water-Served) | Air Handling — Basement / Podium BOH | 2F | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 126 | 126 | 12 | 100 | 100 I/O points carried, 126C cable; length 12 m (typical_range:plant_room_same_room)
C0002 | BMS-PNL-BOHAHU-2F | AHU-2/B.2/B.3/PP/CL/FRE/FRD (ME Contractor) | AHU (Chilled-Water-Served) | Air Handling — Basement / Podium BOH | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 23 | 24 | 12 | 20 | 20 I/O points carried, 24C cable; length 12 m (typical_range:plant_room_same_room)
C0003 | BMS-PNL-AHU-RD | AHU-RD (with CHW mod valve) (BMS Contractor) | AHU (Chilled-Water-Served) | Air Handling — Roofdeck AHU | RD | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 25 | 25 | 16 | 20 | 20 I/O points carried, 25C cable; length 16 m (measured)
C0004 | BMS-PNL-AHU-RD | AHU-RD (with CHW mod valve) (ME Contractor) | AHU (Chilled-Water-Served) | Air Handling — Roofdeck AHU | RD | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 14 | 16 | 14 | 12 | 12 I/O points carried, 16C cable; length 14 m (measured)
C0005 | BMS-PNL-CHWPLANT-2F | CDWP-1 to CDWP-3 (ME Contractor) | Condenser Water Pump | Chilled Water Plant | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 13 | 16 | 12 | 12 | 12 I/O points carried, 16C cable; length 12 m (typical_range:plant_room_same_room)
C0006 | BMS-PNL-CHWPLANT-2F | CH-1 to CH-3 (BMS Contractor) | Chiller (Package Water-Cooled) | Chilled Water Plant | 2F | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 34 | 34 | 14 | 27 | 27 I/O points carried, 34C cable; length 14 m (measured)
C0007 | BMS-PNL-CHWPLANT-2F | CH-1 to CH-3 (ME Contractor) | Chiller (Package Water-Cooled) | Chilled Water Plant | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 62 | 62 | 12 | 54 | 54 I/O points carried, 62C cable; length 12 m (measured)
C0008 | BMS-PNL-CHWPLANT-2F | CHW Supply & Return Main Header (BMS Contractor) | CHW Supply Main Header | Chilled Water Plant | 2F | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 9 | 12 | 8 | 7 | 7 I/O points carried, 12C cable; length 8 m (measured)
C0009 | BMS-PNL-CHWPLANT-2F | CHWP-1 to CHWP-3 (ME Contractor) | Primary CHW Pump | Chilled Water Plant | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 24 | 24 | 10 | 21 | 21 I/O points carried, 24C cable; length 10 m (measured)
C0010 | BMS-PNL-CT-RD | CT-1 to CT-3 (BMS Contractor) | Cooling Tower | Heat Rejection — Cooling Tower | RD | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 30 | 30 | 18 | 24 | 24 I/O points carried, 30C cable; length 18 m (measured)
C0011 | BMS-PNL-CT-RD | CT-1 to CT-3 (ME Contractor) | Cooling Tower | Heat Rejection — Cooling Tower | RD | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 12 | 12 | 16 | 11 | 11 I/O points carried, 12C cable; length 16 m (measured)
C0012 | BMS-PNL-CASINO-2F | DOAS (Casino) — 2 units (BMS Contractor) | DOAS Unit | Casino MVAC — Dedicated Outdoor Air | 2F | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 28 | 28 | 26 | 22 | 22 I/O points carried, 28C cable; length 26 m (measured)
C0013 | BMS-PNL-CASINO-2F | DOAS (Casino) — 2 units (ME Contractor) | DOAS Unit | Casino MVAC — Dedicated Outdoor Air | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 5 | 6 | 24 | 4 | 4 I/O points carried, 6C cable; length 24 m (measured)
C0014 | BMS-PNL-VENT-RD | EF-RD.1/RD.2, EF-1 (ME Contractor) | Exhaust Fan (General) | General Ventilation | RD | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 10 | 12 | 14 | 9 | 9 I/O points carried, 12C cable; length 14 m (measured)
C0015 | BMS-PNL-PLUMBING-LG | HW Supply & Return Header (LG) (BMS Contractor) | CHW Supply Main Header | Plumbing — Sanitary Hot Water | LG | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 8 | 8 | 10 | 6 | 6 I/O points carried, 8C cable; length 10 m (measured)
C0016 | BMS-PNL-PLUMBING-RD | HWT-HZ (×3) (BMS Contractor) | Calorifier (Hot Water Storage Tank) | Plumbing — Sanitary Hot Water | RD | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 4 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (measured)
C0017 | BMS-PNL-PLUMBING-LG | HWT-LZ (×3) (BMS Contractor) | Calorifier (Hot Water Storage Tank) | Plumbing — Sanitary Hot Water | LG | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 4 | 4 | 14 | 3 | 3 I/O points carried, 4C cable; length 14 m (measured)
C0018 | BMS-PNL-AHU-2F | PAHU-0.1 (BMS Contractor) | Precooled Air Handling Unit | Air Handling — Pre-cooled | 2F | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 10 | 12 | 12 | 8 | 8 I/O points carried, 12C cable; length 12 m (typical_range:plant_room_same_room)
C0019 | BMS-PNL-AHU-2F | PAHU-0.1 (ME Contractor) | Precooled Air Handling Unit | Air Handling — Pre-cooled | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 5 | 6 | 12 | 4 | 4 I/O points carried, 6C cable; length 12 m (typical_range:plant_room_same_room)
C0020 | BMS-PNL-AHU-RD | PAHU-RD (×2) (BMS Contractor) | Precooled Air Handling Unit | Air Handling — Pre-cooled (Roofdeck) | RD | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 5 | 6 | 14 | 4 | 4 I/O points carried, 6C cable; length 14 m (measured)
C0021 | BMS-PNL-AHU-RD | PAHU-RD (×2) (ME Contractor) | Precooled Air Handling Unit | Air Handling — Pre-cooled (Roofdeck) | RD | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 9 | 12 | 12 | 8 | 8 I/O points carried, 12C cable; length 12 m (measured)
C0022 | BMS-PNL-PLUMBING-RD | RP-HZ (×3) (ME Contractor) | Recirculating Pump | Plumbing — Sanitary Hot Water | RD | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 10 | 12 | 12 | 9 | 9 I/O points carried, 12C cable; length 12 m (typical_range:plant_room_same_room)
C0023 | BMS-PNL-PLUMBING-LG | RP-LZ (×3) (ME Contractor) | Recirculating Pump | Plumbing — Sanitary Hot Water | LG | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 10 | 12 | 12 | 9 | 9 I/O points carried, 12C cable; length 12 m (typical_range:plant_room_same_room)
C0024 | BMS-PNL-BOILER-LG | SB-1 & SB-2 (BMS Contractor) | Steam Boiler | Boiler / Laundry | LG | 4C × 1.5 mm² shielded FRLS (BMS sensor signal) | 8 | 8 | 12 | 6 | 6 I/O points carried, 8C cable; length 12 m (measured)
C0025 | BMS-PNL-BOILER-LG | SB-1 & SB-2 (ME Contractor) | Steam Boiler | Boiler / Laundry | LG | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 18 | 20 | 10 | 16 | 16 I/O points carried, 20C cable; length 10 m (measured)
C0026 | BMS-PNL-CASINO-2F | Sanitizer for AHU-2M.1/2M.2 (Equipment Supplier) | Ozone Generator (UV-light or Corona) | Casino MVAC — Smoke Sanitizer | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 5 | 6 | 28 | 4 | 4 I/O points carried, 6C cable; length 28 m (typical_range:casino_floor_field)
C0027 | BMS-PNL-VENT-GF | TEF-1.1 to 1.4 + EF-1.2A/LPG.1/1MR.1/1STO.1/MRF.1 (ME Contractor) | Exhaust Fan (General) | General Ventilation | GF | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 31 | 31 | 35 | 27 | 27 I/O points carried, 31C cable; length 35 m (typical_range:guestroom_corridor)
C0028 | BMS-PNL-VENT-2F | TEF-2.1/2.3/2B.3 + EF-2B.1/2B.2/GS.1&GS.2 + EF-2.1 to 2.4 + EF-CHRx2 (ME Contractor) | Exhaust Fan (General) | General Ventilation | 2F | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 45 | 45 | 35 | 39 | 39 I/O points carried, 45C cable; length 35 m (typical_range:guestroom_corridor)
C0029 | BMS-PNL-VENT-3F | TEF-3Ax2/3B/3Cx2/3Dx20 + others (ME Contractor) | Exhaust Fan (General) | General Ventilation | 3F | 4C × 1.5 mm² FRLS (equipment aux contacts — status / H-O-A / trip) | 93 | 93 | 35 | 81 | 81 I/O points carried, 93C cable; length 35 m (typical_range:guestroom_corridor)

## Trunks
ID | From | To | Cable Type | Length (m) | Notes
T0030 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for 2nd Floor — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0031 | BMS Server Room (head-end) | BMS panel controllers (per topology id mstp_main_backbone) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 320 | Daisy-chain across the 13 BMS field panels. Path: Boiler-LG → Plumbing-LG → CHWPlant-2F → BOH-AHU-2F → AHU-2F → Casino-2F → Vent-GF → Vent-2F → Vent-3F → Vent-RD → AHU-RD → CT-RD → Plumbing-RD. Routed via riser shaft per EE-24 + horizontal corridor tray on each floor (per ECE auxiliary plans).

## Panel Power Feeds
ID | From | To | Cable Type | Length (m) | Notes
P0032 | Local panelboard / EE-supplied feeder | BMS-PNL-AHU-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)
P0033 | Local panelboard / EE-supplied feeder | BMS-PNL-AHU-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)
P0034 | Local panelboard / EE-supplied feeder | BMS-PNL-BOHAHU-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)
P0035 | Local panelboard / EE-supplied feeder | BMS-PNL-BOILER-LG — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)
P0036 | Local panelboard / EE-supplied feeder | BMS-PNL-CASINO-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)
P0037 | Local panelboard / EE-supplied feeder | BMS-PNL-CHWPLANT-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)
P0038 | Local panelboard / EE-supplied feeder | BMS-PNL-CT-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)
P0039 | Local panelboard / EE-supplied feeder | BMS-PNL-PLUMBING-LG — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)
P0040 | Local panelboard / EE-supplied feeder | BMS-PNL-PLUMBING-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)
P0041 | Local panelboard / EE-supplied feeder | BMS-PNL-VENT-2F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)
P0042 | Local panelboard / EE-supplied feeder | BMS-PNL-VENT-3F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)
P0043 | Local panelboard / EE-supplied feeder | BMS-PNL-VENT-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)
P0044 | Local panelboard / EE-supplied feeder | BMS-PNL-VENT-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 18 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 18 m (typical_range:bms_panel_power_feed)