## Summary
A4 — Panel Schedule Summary
Total panels | 13
Total physical I/O | 570
Total HLI subpoints | 49
Total network drops | 0
Total I/O points | 619
Estimated total controllers | 21
Estimated total power (W) | 525

## Panel Schedule
Panel | Location | System Scope | Equipment Count | Physical I/O | HLI Subpoints | Network Drops | Total I/O | DDC Controllers | Network Gateway | Total Controllers | Power (W) | Enclosure
BMS-PNL-AHU-2F | 2F | Air Handling — Pre-cooled | 1 | 12 | 4 | 0 | 16 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-AHU-RD | RD | Air Handling — Pre-cooled (Roofdeck), Air Handling — Roofdeck AHU | 2 | 44 | 2 | 0 | 46 | 2 | 0 | 2 | 50 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-BOHAHU-2F | 2F | Air Handling — Basement / Podium BOH | 1 | 120 | 20 | 0 | 140 | 3 | 0 | 3 | 75 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-BOILER-LG | LG | Boiler / Laundry | 1 | 22 | 0 | 0 | 22 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-CASINO-2F | 2F | Casino MVAC — Dedicated Outdoor Air, Casino MVAC — Smoke Sanitizer | 2 | 30 | 4 | 0 | 34 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-CHWPLANT-2F | 2F | Chilled Water Plant | 4 | 121 | 0 | 0 | 121 | 4 | 0 | 4 | 100 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-CT-RD | RD | Heat Rejection — Cooling Tower | 1 | 35 | 1 | 0 | 36 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-PLUMBING-LG | LG | Plumbing — Sanitary Hot Water | 4 | 18 | 9 | 0 | 27 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-PLUMBING-RD | RD | Plumbing — Sanitary Hot Water | 3 | 12 | 9 | 0 | 21 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-VENT-2F | 2F | General Ventilation | 1 | 39 | 0 | 0 | 39 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-VENT-3F | 3F | General Ventilation | 1 | 81 | 0 | 0 | 81 | 3 | 0 | 3 | 75 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-VENT-GF | GF | General Ventilation | 1 | 27 | 0 | 0 | 27 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
BMS-PNL-VENT-RD | RD | General Ventilation | 1 | 9 | 0 | 0 | 9 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare

## Equipment per Panel
Panel | Equipment Instance
BMS-PNL-AHU-2F | PAHU-0.1
BMS-PNL-AHU-RD | AHU-RD (with CHW mod valve)
BMS-PNL-AHU-RD | PAHU-RD (×2)
BMS-PNL-BOHAHU-2F | AHU-2/B.2/B.3/PP/CL/FRE/FRD
BMS-PNL-BOILER-LG | SB-1 & SB-2
BMS-PNL-CASINO-2F | DOAS (Casino) — 2 units
BMS-PNL-CASINO-2F | Sanitizer for AHU-2M.1/2M.2
BMS-PNL-CHWPLANT-2F | CDWP-1 to CDWP-3
BMS-PNL-CHWPLANT-2F | CH-1 to CH-3
BMS-PNL-CHWPLANT-2F | CHW Supply & Return Main Header
BMS-PNL-CHWPLANT-2F | CHWP-1 to CHWP-3
BMS-PNL-CT-RD | CT-1 to CT-3
BMS-PNL-PLUMBING-LG | HP-LZ (×3)
BMS-PNL-PLUMBING-LG | HW Supply & Return Header (LG)
BMS-PNL-PLUMBING-LG | HWT-LZ (×3)
BMS-PNL-PLUMBING-LG | RP-LZ (×3)
BMS-PNL-PLUMBING-RD | HP-HZ (×3)
BMS-PNL-PLUMBING-RD | HWT-HZ (×3)
BMS-PNL-PLUMBING-RD | RP-HZ (×3)
BMS-PNL-VENT-2F | TEF-2.1/2.3/2B.3 + EF-2B.1/2B.2/GS.1&GS.2 + EF-2.1 to 2.4 + EF-CHRx2
BMS-PNL-VENT-3F | TEF-3Ax2/3B/3Cx2/3Dx20 + others
BMS-PNL-VENT-GF | TEF-1.1 to 1.4 + EF-1.2A/LPG.1/1MR.1/1STO.1/MRF.1
BMS-PNL-VENT-RD | EF-RD.1/RD.2, EF-1