## Summary
A3 — Cable Schedule, Audit View
Project | Kingsford Hotel Bacolod — BMS
Canonical source | A3-cable-schedule.yaml
How to record corrections | Edit the canonical YAML directly — add a verification: block to the affected row(s)
Totals
Total cables | 220
Total length (m) | 5,173
Field cables | 205
Trunk cables | 7
Panel power feeds | 8
Verification status
Status | Count | % of total
verified | 0 | 0%
needs_correction | 0 | 0%
uncertain | 0 | 0%
unverified | 220 | 100%
⚠ Known weak points
Cable lengths are estimates based on assumption A-001 (30 m average panel-to-device run, 80 m trunk per floor). Field-verified lengths typically vary by ±20% per cable. THIS IS THE SYSTEM'S WEAKEST AUTO-GENERATED QUANTITY — please verify before issuing the BOQ to the customer.
How corrections flow
1. Open A3-cable-schedule.yaml in any text editor.
2. Find the affected row by ID (column A in the Detail sheet).
3. Add a verification: block — see the 'Verification schema' sheet for the template.
4. Re-run: python3 _playbook/tools/generate-deliverables.py <project>
5. Corrections flow through B4 manhours, BOQ material costs, and final deliverables automatically.

## By Panel
Panel | Cable count | Total length (m)
DDC-2F-BOH | 61 | 1525
DDC-B1-BOH | 20 | 560
DDC-RD-PLANT | 34 | 510
DDC-GF-BOH | 18 | 450
DDC-3F | 12 | 420
DDC-2F-CHILLER | 29 | 348
DDC-2M-CASINO | 18 | 324
DDC-LG-PLANT | 13 | 156
TOTAL (field cables) | 205 | 4293

## By Floor
Floor | Cable count | Total length (m)
2nd Floor | 90 | 1873
Basement | 20 | 560
Roofdeck | 34 | 510
Ground | 18 | 450
3rd Floor | 12 | 420
2nd Mezzanine (Casino) | 18 | 324
Lower Ground | 13 | 156
TOTAL | 205 | 4293

## By Cable Type
Cable type | Count | Total length (m)
4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 90 | 2097
4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 44 | 802
Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 42 | 796
4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 29 | 598

## Detail (cables)
ID | From | To | Cable type | Length (m) | Status | Corrected (m) | Verified by | Date | Drawing ref | Notes
C0001 | DDC-GF-BOH | AHU-1.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0002 | DDC-GF-BOH | AHU-1.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0003 | DDC-GF-BOH | AHU-1.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0004 | DDC-GF-BOH | AHU-1.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0005 | DDC-GF-BOH | AHU-1.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0006 | DDC-GF-BOH | AHU-1.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0007 | DDC-GF-BOH | AHU-1.3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0008 | DDC-GF-BOH | AHU-1.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0009 | DDC-GF-BOH | AHU-1.3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0010 | DDC-2M-CASINO | AHU-2M.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 18 | unverified
C0011 | DDC-2M-CASINO | AHU-2M.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 18 | unverified
C0012 | DDC-2M-CASINO | AHU-2M.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 18 | unverified
C0013 | DDC-2M-CASINO | AHU-2M.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 18 | unverified
C0014 | DDC-2M-CASINO | AHU-2M.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 18 | unverified
C0015 | DDC-2M-CASINO | AHU-2M.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 18 | unverified
C0016 | DDC-2F-BOH | AHU-B.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0017 | DDC-2F-BOH | AHU-B.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0018 | DDC-2F-BOH | AHU-B.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0019 | DDC-2F-BOH | AHU-B.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0020 | DDC-2F-BOH | AHU-B.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0021 | DDC-2F-BOH | AHU-B.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0022 | DDC-2F-BOH | AHU-B.3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0023 | DDC-2F-BOH | AHU-B.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0024 | DDC-2F-BOH | AHU-B.3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0025 | DDC-2F-BOH | AHU-EL (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0026 | DDC-2F-BOH | AHU-EL (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0027 | DDC-2F-BOH | AHU-EL (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0028 | DDC-2F-BOH | AHU-FR2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0029 | DDC-2F-BOH | AHU-FR2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0030 | DDC-2F-BOH | AHU-FR2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0031 | DDC-2F-BOH | AHU-FR3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0032 | DDC-2F-BOH | AHU-FR3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0033 | DDC-2F-BOH | AHU-FR3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0034 | DDC-2F-BOH | AHU-PF (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0035 | DDC-2F-BOH | AHU-PF (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0036 | DDC-2F-BOH | AHU-PF (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0037 | DDC-2M-CASINO | AIR-ION-2M.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 18 | unverified
C0038 | DDC-2M-CASINO | AIR-ION-2M.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 18 | unverified
C0039 | DDC-2M-CASINO | AIR-ION-2M.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 18 | unverified
C0040 | DDC-2M-CASINO | AIR-ION-2M.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 18 | unverified
C0041 | DDC-2F-CHILLER | CH-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 12 | unverified
C0042 | DDC-2F-CHILLER | CH-1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 12 | unverified
C0043 | DDC-2F-CHILLER | CH-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 12 | unverified
C0044 | DDC-2F-CHILLER | CH-2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 12 | unverified
C0045 | DDC-2F-CHILLER | CH-3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 12 | unverified
C0046 | DDC-2F-CHILLER | CH-3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 12 | unverified
C0047 | DDC-2F-CHILLER | CHW-DIFF (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 12 | unverified
C0048 | DDC-2F-CHILLER | CHW-RET-HDR (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 12 | unverified
C0049 | DDC-2F-CHILLER | CHW-SUP-HDR (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 12 | unverified
C0050 | DDC-2F-CHILLER | COWP-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0051 | DDC-2F-CHILLER | COWP-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0052 | DDC-2F-CHILLER | COWP-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0053 | DDC-RD-PLANT | CT-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 15 | unverified
C0054 | DDC-RD-PLANT | CT-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 15 | unverified
C0055 | DDC-RD-PLANT | CT-1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 15 | unverified
C0056 | DDC-RD-PLANT | CT-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 15 | unverified
C0057 | DDC-RD-PLANT | CT-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 15 | unverified
C0058 | DDC-RD-PLANT | CT-2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 15 | unverified
C0059 | DDC-RD-PLANT | CT-3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 15 | unverified
C0060 | DDC-RD-PLANT | CT-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 15 | unverified
C0061 | DDC-RD-PLANT | CT-3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 15 | unverified
C0062 | DDC-RD-PLANT | CT-COMMON (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 15 | unverified
C0063 | DDC-RD-PLANT | CW-HDR (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 15 | unverified
C0064 | DDC-2M-CASINO | DOAS-2M (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 18 | unverified
C0065 | DDC-2M-CASINO | DOAS-2M (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 18 | unverified
C0066 | DDC-2M-CASINO | DOAS-2M (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 18 | unverified
C0067 | DDC-RD-PLANT | DOAS-RD.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 15 | unverified
C0068 | DDC-RD-PLANT | DOAS-RD.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 15 | unverified
C0069 | DDC-RD-PLANT | DOAS-RD.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 15 | unverified
C0070 | DDC-RD-PLANT | DOAS-RD.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 15 | unverified
C0071 | DDC-RD-PLANT | DOAS-RD.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 15 | unverified
C0072 | DDC-RD-PLANT | DOAS-RD.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 15 | unverified
C0073 | DDC-RD-PLANT | EF-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 15 | unverified
C0074 | DDC-2F-BOH | EF-2.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0075 | DDC-2F-BOH | EF-2.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0076 | DDC-2F-BOH | EF-2.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0077 | DDC-2F-BOH | EF-2.4 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0078 | DDC-2F-BOH | EF-2B.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0079 | DDC-2F-BOH | EF-2B.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0080 | DDC-3F | EF-3.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 35 | unverified
C0081 | DDC-3F | EF-3.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 35 | unverified
C0082 | DDC-3F | EF-3.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 35 | unverified
C0083 | DDC-3F | EF-3.4 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 35 | unverified
C0084 | DDC-3F | EF-3B-G (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 35 | unverified
C0085 | DDC-3F | EF-3C.1-G (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 35 | unverified
C0086 | DDC-B1-BOH | EF-B.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0087 | DDC-B1-BOH | EF-B.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0088 | DDC-B1-BOH | EF-BR.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0089 | DDC-B1-BOH | EF-BR.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0090 | DDC-B1-BOH | EF-BS.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0091 | DDC-B1-BOH | EF-BS.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0092 | DDC-B1-BOH | EF-FOST.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0093 | DDC-B1-BOH | EF-GL.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0094 | DDC-B1-BOH | EF-GL.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0095 | DDC-2F-BOH | EF-GS.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0096 | DDC-2F-BOH | EF-GS.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0097 | DDC-B1-BOH | EF-MFR.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0098 | DDC-B1-BOH | EF-MP.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0099 | DDC-2F-BOH | EF-OHRv2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0100 | DDC-B1-BOH | EF-PR.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0101 | DDC-B1-BOH | EF-PR.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0102 | DDC-RD-PLANT | EF-RD.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 15 | unverified
C0103 | DDC-RD-PLANT | EF-RO.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 15 | unverified
C0104 | DDC-B1-BOH | EF-WS.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0105 | DDC-RD-PLANT | HP-HZ (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 15 | unverified
C0106 | DDC-LG-PLANT | HP-LZ (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0107 | DDC-RD-PLANT | HWH-HZ (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 15 | unverified
C0108 | DDC-LG-PLANT | HWH-LZ (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 12 | unverified
C0109 | DDC-RD-PLANT | HWT-HZ (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 15 | unverified
C0110 | DDC-LG-PLANT | HWT-LZ (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 12 | unverified
C0111 | DDC-B1-BOH | PAHU-0.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 28 | unverified
C0112 | DDC-B1-BOH | PAHU-0.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0113 | DDC-B1-BOH | PAHU-0.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 28 | unverified
C0114 | DDC-2F-BOH | PAHU-B.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0115 | DDC-2F-BOH | PAHU-B.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0116 | DDC-2F-BOH | PAHU-B.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0117 | DDC-2F-BOH | PAHU-B.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0118 | DDC-2F-BOH | PAHU-B.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0119 | DDC-2F-BOH | PAHU-B.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0120 | DDC-2F-BOH | PAHU-B.3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0121 | DDC-2F-BOH | PAHU-B.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0122 | DDC-2F-BOH | PAHU-B.3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0123 | DDC-2F-BOH | PAHU-FR (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0124 | DDC-2F-BOH | PAHU-FR (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0125 | DDC-2F-BOH | PAHU-FR (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0126 | DDC-2F-BOH | PAHU-PF (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 25 | unverified
C0127 | DDC-2F-BOH | PAHU-PF (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0128 | DDC-2F-BOH | PAHU-PF (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 25 | unverified
C0129 | DDC-RD-PLANT | PAHU-r.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 15 | unverified
C0130 | DDC-RD-PLANT | PAHU-r.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 15 | unverified
C0131 | DDC-RD-PLANT | PAHU-r.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 15 | unverified
C0132 | DDC-RD-PLANT | PAHU-r.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 15 | unverified
C0133 | DDC-RD-PLANT | PAHU-r.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 15 | unverified
C0134 | DDC-RD-PLANT | PAHU-r.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 15 | unverified
C0135 | DDC-2F-CHILLER | PCHWP-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 12 | unverified
C0136 | DDC-2F-CHILLER | PCHWP-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0137 | DDC-2F-CHILLER | PCHWP-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 12 | unverified
C0138 | DDC-2F-CHILLER | PCHWP-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0139 | DDC-2F-CHILLER | PCHWP-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0140 | DDC-RD-PLANT | RP-HZ (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 15 | unverified
C0141 | DDC-LG-PLANT | RP-LZ (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0142 | DDC-LG-PLANT | SB-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 12 | unverified
C0143 | DDC-LG-PLANT | SB-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0144 | DDC-LG-PLANT | SB-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 12 | unverified
C0145 | DDC-LG-PLANT | SB-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0146 | DDC-2F-CHILLER | SCHWP-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0147 | DDC-2F-CHILLER | SCHWP-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0148 | DDC-2F-CHILLER | SCHWP-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 12 | unverified
C0149 | DDC-GF-BOH | TEF-1.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0150 | DDC-GF-BOH | TEF-1.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0151 | DDC-GF-BOH | TEF-1.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0152 | DDC-GF-BOH | TEF-1.4 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0153 | DDC-2F-BOH | TEF-2.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0154 | DDC-2F-BOH | TEF-2.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0155 | DDC-2F-BOH | TEF-2B.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 25 | unverified
C0156 | DDC-3F | TEF-30.20 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 35 | unverified
C0157 | DDC-3F | TEF-3A.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 35 | unverified
C0158 | DDC-3F | TEF-3A.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 35 | unverified
C0159 | DDC-3F | TEF-3B (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 35 | unverified
C0160 | DDC-3F | TEF-3C.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 35 | unverified
C0161 | DDC-3F | TEF-3C.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 35 | unverified
C0162 | DDC-B1-BOH | TEF-B.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0163 | DDC-B1-BOH | TEF-B.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 28 | unverified
C0164 | DDC-2F-CHILLER | CH-1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0165 | DDC-2F-CHILLER | CH-2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0166 | DDC-2F-CHILLER | CH-3 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0167 | DDC-2F-CHILLER | PCHWP-1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0168 | DDC-2F-CHILLER | PCHWP-2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0169 | DDC-2F-CHILLER | SCHWP-1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0170 | DDC-2F-CHILLER | SCHWP-2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0171 | DDC-2F-CHILLER | SCHWP-3 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0172 | DDC-LG-PLANT | SB-1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0173 | DDC-LG-PLANT | SB-2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0174 | DDC-RD-PLANT | DOAS-RD.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 15 | unverified
C0175 | DDC-RD-PLANT | DOAS-RD.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 15 | unverified
C0176 | DDC-RD-PLANT | PAHU-r.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 15 | unverified
C0177 | DDC-RD-PLANT | PAHU-r.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 15 | unverified
C0178 | DDC-2M-CASINO | DOAS-2M (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 18 | unverified
C0179 | DDC-2M-CASINO | AHU-2M.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 18 | unverified
C0180 | DDC-2M-CASINO | AHU-2M.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 18 | unverified
C0181 | DDC-2M-CASINO | AIR-ION-2M.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 18 | unverified
C0182 | DDC-2M-CASINO | AIR-ION-2M.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 18 | unverified
C0183 | DDC-2F-BOH | AHU-B.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0184 | DDC-2F-BOH | AHU-B.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0185 | DDC-2F-BOH | AHU-B.3 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0186 | DDC-2F-BOH | AHU-PF (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0187 | DDC-2F-BOH | AHU-EL (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0188 | DDC-2F-BOH | AHU-FR2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0189 | DDC-2F-BOH | AHU-FR3 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0190 | DDC-2F-BOH | PAHU-B.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0191 | DDC-2F-BOH | PAHU-B.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0192 | DDC-2F-BOH | PAHU-B.3 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0193 | DDC-2F-BOH | PAHU-PF (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0194 | DDC-2F-BOH | PAHU-FR (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0195 | DDC-GF-BOH | AHU-1.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0196 | DDC-GF-BOH | AHU-1.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0197 | DDC-GF-BOH | AHU-1.3 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0198 | DDC-B1-BOH | PAHU-0.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 28 | unverified
C0199 | DDC-LG-PLANT | MPM-MAIN (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0200 | DDC-2F-CHILLER | MPM-CHILLER (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0201 | DDC-2F-BOH | MPM-AHU-2F (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0202 | DDC-GF-BOH | MPM-AHU-GF (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
C0203 | DDC-LG-PLANT | MPM-LIGHT-A (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0204 | DDC-LG-PLANT | MPM-LIGHT-B (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 12 | unverified
C0205 | DDC-GF-BOH | FACP-GW (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 25 | unverified
T0206 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0207 | BMS Server Room (head-end) | All BMS panels at 3rd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0208 | BMS Server Room (head-end) | All BMS panels at Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0209 | BMS Server Room (head-end) | All BMS panels at Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0210 | BMS Server Room (head-end) | All BMS panels at Lower Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0211 | BMS Server Room (head-end) | BMS panel controllers (per topology id mstp_field_backbone) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 250 | unverified
T0212 | BMS Server Room (head-end) | BMS panel controllers (per topology id bacnet_ip_backbone) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 150 | unverified
P0213 | Local panelboard / EE-supplied feeder | DDC-2F-BOH — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | unverified
P0214 | Local panelboard / EE-supplied feeder | DDC-2F-CHILLER — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | unverified
P0215 | Local panelboard / EE-supplied feeder | DDC-2M-CASINO — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | unverified
P0216 | Local panelboard / EE-supplied feeder | DDC-3F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | unverified
P0217 | Local panelboard / EE-supplied feeder | DDC-B1-BOH — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | unverified
P0218 | Local panelboard / EE-supplied feeder | DDC-GF-BOH — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | unverified
P0219 | Local panelboard / EE-supplied feeder | DDC-LG-PLANT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | unverified
P0220 | Local panelboard / EE-supplied feeder | DDC-RD-PLANT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | unverified

## Verification schema
How to record verification / corrections in A3-cable-schedule.yaml
Find the affected row in the YAML by ID (Detail sheet column A) and add a verification: block:
- id: C0001
from: PNL-CH-PLANT-GND
to: CH-1 (BMS Contractor)
cable_type: 4C × 1.5 mm² shielded FRLS
length_m: 30
verification: # ADDED by team
status: needs_correction # unverified ¦ verified ¦ needs_correction ¦ uncertain
corrected_length_m: 42 # team's measured / confirmed value
verified_by: J. Cruz
verified_date: 2026-05-10
drawing_ref: "EE-09 grid B-2"
notes: ""
After saving, re-run: python3 _playbook/tools/generate-deliverables.py <project>
Corrections propagate to B4 manhours, BOQ, and final deliverables automatically.
Recommended verification methods (priority order):
1. Site walkthrough with measurement (most accurate; for cable lengths, after structural completion).
2. Properly-scaled architectural drawings.
3. Mechanical contractor's tray layout combined with BMS panel locations.
4. A-001 default with ±20% contingency in BOQ — last resort.