## Summary
A1 — Consolidated I/O List Summary
Project | Kingsford Hotel Bacolod — BMS
Total I/O rows | 744
By type
DI | 286
AI | 200
HLI | 141
AO | 58
Network | 42
DO | 17
By C/O
Equipment Supplier | 490
BMS Contractor | 183
ME Contractor | 67
EE Contractor | 4
By system
AC | 365
VENT | 343
HWL | 20
EL | 12
FDAS | 4
By panel
DDC-2F-BOH | 203
DDC-2F-CHILLER | 146
DDC-RD-PLANT | 126
DDC-GF-BOH | 63
DDC-2M-CASINO | 60
DDC-B1-BOH | 60
DDC-LG-PLANT | 50
DDC-3F | 36

## All IO Points
ID | System | Equipment Class | Equipment Instance | Location | Point Description | Type | Field Device | C/O | DoO Ref | Panel | Source | Notes
P-0001 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Entering Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0002 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Leaving Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0003 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Isolation Motorized Valve Status CHW Return & Supply | DI | Electric Valve Actuator | ME Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0004 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Entering Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0005 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Leaving Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0006 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Isolation Motorized Valve Status COW Return & Supply | DI | Electric Valve Actuator | ME Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0007 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Chilled Water Return Flow Metering | AI | Flow Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0008 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Chilled Water Supply Flow Metering | AI | Flow Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0009 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Condenser Water Supply Flow Metering | AI | Flow Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0010 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Network drop (BACnet/IP — chiller plant manager gateway) | Network | Chiller PLC + BACnet gateway | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0011 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Chiller Compressor Pump On/Off Status | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0012 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Chiller Compressor Hand/Off/Auto Status | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0013 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Chiller Compressor Trip Alarm Status | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0014 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Motor Load Current | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0015 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Motor Consumption — KW / BTU Meter | HLI | Chiller PLC + BTU meter | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0016 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Winding Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0017 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Evaporator Approach Delta Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0018 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Evaporator Approach Delta Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0019 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Evaporator Refrigerant Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0020 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Evaporator Refrigerant Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0021 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Condenser Refrigerant Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0022 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Condenser Refrigerant Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0023 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Condenser Approach Delta Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0024 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Condenser Approach Delta Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0025 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Oil Sump Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0026 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Oil Sump Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0027 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Oil Pump Status (ON/OFF) | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0028 | AC | Chiller (Package Water-Cooled) | CH-1 | 2nd Level Chiller Room | Oil Pump Trip Status | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0029 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Entering Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0030 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Leaving Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0031 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Isolation Motorized Valve Status CHW Return & Supply | DI | Electric Valve Actuator | ME Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0032 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Entering Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0033 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Leaving Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0034 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Isolation Motorized Valve Status COW Return & Supply | DI | Electric Valve Actuator | ME Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0035 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Chilled Water Return Flow Metering | AI | Flow Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0036 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Chilled Water Supply Flow Metering | AI | Flow Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0037 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Condenser Water Supply Flow Metering | AI | Flow Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0038 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Network drop (BACnet/IP — chiller plant manager gateway) | Network | Chiller PLC + BACnet gateway | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0039 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Chiller Compressor Pump On/Off Status | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0040 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Chiller Compressor Hand/Off/Auto Status | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0041 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Chiller Compressor Trip Alarm Status | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0042 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Motor Load Current | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0043 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Motor Consumption — KW / BTU Meter | HLI | Chiller PLC + BTU meter | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0044 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Winding Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0045 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Evaporator Approach Delta Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0046 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Evaporator Approach Delta Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0047 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Evaporator Refrigerant Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0048 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Evaporator Refrigerant Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0049 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Condenser Refrigerant Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0050 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Condenser Refrigerant Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0051 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Condenser Approach Delta Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0052 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Condenser Approach Delta Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0053 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Oil Sump Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0054 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Oil Sump Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0055 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Oil Pump Status (ON/OFF) | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0056 | AC | Chiller (Package Water-Cooled) | CH-2 | 2nd Level Chiller Room | Oil Pump Trip Status | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0057 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Entering Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0058 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Leaving Chilled Water Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0059 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Isolation Motorized Valve Status CHW Return & Supply | DI | Electric Valve Actuator | ME Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0060 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Entering Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0061 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Leaving Condenser Water Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0062 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Isolation Motorized Valve Status COW Return & Supply | DI | Electric Valve Actuator | ME Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0063 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Chilled Water Return Flow Metering | AI | Flow Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0064 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Chilled Water Supply Flow Metering | AI | Flow Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0065 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Condenser Water Supply Flow Metering | AI | Flow Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0066 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Network drop (BACnet/IP — chiller plant manager gateway) | Network | Chiller PLC + BACnet gateway | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0067 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Chiller Compressor Pump On/Off Status | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0068 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Chiller Compressor Hand/Off/Auto Status | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0069 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Chiller Compressor Trip Alarm Status | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0070 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Motor Load Current | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0071 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Motor Consumption — KW / BTU Meter | HLI | Chiller PLC + BTU meter | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0072 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Winding Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0073 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Evaporator Approach Delta Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0074 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Evaporator Approach Delta Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0075 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Evaporator Refrigerant Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0076 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Evaporator Refrigerant Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0077 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Condenser Refrigerant Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0078 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Condenser Refrigerant Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0079 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Condenser Approach Delta Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0080 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Condenser Approach Delta Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0081 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Oil Sump Pressure | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0082 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Oil Sump Temperature | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0083 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Oil Pump Status (ON/OFF) | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0084 | AC | Chiller (Package Water-Cooled) | CH-3 | 2nd Level Chiller Room | Oil Pump Trip Status | HLI | Chiller PLC | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0085 | AC | Primary CHW Pump | PCHWP-1 | 2nd Level Chiller Room | Pump On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0086 | AC | Primary CHW Pump | PCHWP-1 | 2nd Level Chiller Room | Pump Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0087 | AC | Primary CHW Pump | PCHWP-1 | 2nd Level Chiller Room | Pump Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0088 | AC | Primary CHW Pump | PCHWP-1 | 2nd Level Chiller Room | Pump Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0089 | AC | Primary CHW Pump | PCHWP-1 | 2nd Level Chiller Room | Chilled Water Supply Pressure | AI | Pressure Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0090 | AC | Primary CHW Pump | PCHWP-1 | 2nd Level Chiller Room | VFD Speed (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0091 | AC | Primary CHW Pump | PCHWP-1 | 2nd Level Chiller Room | VFD Speed Command (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0092 | AC | Primary CHW Pump | PCHWP-1 | 2nd Level Chiller Room | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0093 | AC | Primary CHW Pump | PCHWP-2 | 2nd Level Chiller Room | Pump On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0094 | AC | Primary CHW Pump | PCHWP-2 | 2nd Level Chiller Room | Pump Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0095 | AC | Primary CHW Pump | PCHWP-2 | 2nd Level Chiller Room | Pump Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0096 | AC | Primary CHW Pump | PCHWP-2 | 2nd Level Chiller Room | Pump Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0097 | AC | Primary CHW Pump | PCHWP-2 | 2nd Level Chiller Room | Chilled Water Supply Pressure | AI | Pressure Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0098 | AC | Primary CHW Pump | PCHWP-2 | 2nd Level Chiller Room | VFD Speed (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0099 | AC | Primary CHW Pump | PCHWP-2 | 2nd Level Chiller Room | VFD Speed Command (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0100 | AC | Primary CHW Pump | PCHWP-2 | 2nd Level Chiller Room | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0101 | AC | Primary CHW Pump (Standby) | PCHWP-3 | 2nd Level Chiller Room | Pump On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0102 | AC | Primary CHW Pump (Standby) | PCHWP-3 | 2nd Level Chiller Room | Pump Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0103 | AC | Primary CHW Pump (Standby) | PCHWP-3 | 2nd Level Chiller Room | Pump Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0104 | AC | Primary CHW Pump (Standby) | PCHWP-3 | 2nd Level Chiller Room | Pump Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0105 | AC | Secondary CHW Pump | SCHWP-1 | 2nd Level Chiller Room | Pump On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0106 | AC | Secondary CHW Pump | SCHWP-1 | 2nd Level Chiller Room | Pump Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0107 | AC | Secondary CHW Pump | SCHWP-1 | 2nd Level Chiller Room | Pump Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0108 | AC | Secondary CHW Pump | SCHWP-1 | 2nd Level Chiller Room | Pump Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0109 | AC | Secondary CHW Pump | SCHWP-1 | 2nd Level Chiller Room | VFD Speed (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0110 | AC | Secondary CHW Pump | SCHWP-1 | 2nd Level Chiller Room | VFD Speed Command (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0111 | AC | Secondary CHW Pump | SCHWP-1 | 2nd Level Chiller Room | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0112 | AC | Secondary CHW Pump | SCHWP-2 | 2nd Level Chiller Room | Pump On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0113 | AC | Secondary CHW Pump | SCHWP-2 | 2nd Level Chiller Room | Pump Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0114 | AC | Secondary CHW Pump | SCHWP-2 | 2nd Level Chiller Room | Pump Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0115 | AC | Secondary CHW Pump | SCHWP-2 | 2nd Level Chiller Room | Pump Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0116 | AC | Secondary CHW Pump | SCHWP-2 | 2nd Level Chiller Room | VFD Speed (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0117 | AC | Secondary CHW Pump | SCHWP-2 | 2nd Level Chiller Room | VFD Speed Command (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0118 | AC | Secondary CHW Pump | SCHWP-2 | 2nd Level Chiller Room | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0119 | AC | Secondary CHW Pump | SCHWP-3 | 2nd Level Chiller Room | Pump On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0120 | AC | Secondary CHW Pump | SCHWP-3 | 2nd Level Chiller Room | Pump Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0121 | AC | Secondary CHW Pump | SCHWP-3 | 2nd Level Chiller Room | Pump Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0122 | AC | Secondary CHW Pump | SCHWP-3 | 2nd Level Chiller Room | Pump Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0123 | AC | Secondary CHW Pump | SCHWP-3 | 2nd Level Chiller Room | VFD Speed (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0124 | AC | Secondary CHW Pump | SCHWP-3 | 2nd Level Chiller Room | VFD Speed Command (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0125 | AC | Secondary CHW Pump | SCHWP-3 | 2nd Level Chiller Room | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0126 | AC | Condenser Water Pump | COWP-1 | 2nd Level Chiller Room | Pump On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0127 | AC | Condenser Water Pump | COWP-1 | 2nd Level Chiller Room | Pump Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0128 | AC | Condenser Water Pump | COWP-1 | 2nd Level Chiller Room | Pump Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0129 | AC | Condenser Water Pump | COWP-1 | 2nd Level Chiller Room | Pump Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0130 | AC | Condenser Water Pump | COWP-2 | 2nd Level Chiller Room | Pump On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0131 | AC | Condenser Water Pump | COWP-2 | 2nd Level Chiller Room | Pump Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0132 | AC | Condenser Water Pump | COWP-2 | 2nd Level Chiller Room | Pump Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0133 | AC | Condenser Water Pump | COWP-2 | 2nd Level Chiller Room | Pump Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0134 | AC | Condenser Water Pump | COWP-3 | 2nd Level Chiller Room | Pump On/Off Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0135 | AC | Condenser Water Pump | COWP-3 | 2nd Level Chiller Room | Pump Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0136 | AC | Condenser Water Pump | COWP-3 | 2nd Level Chiller Room | Pump Trip Alarm | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0137 | AC | Condenser Water Pump | COWP-3 | 2nd Level Chiller Room | Pump Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0138 | AC | CHW Supply Main Header | CHW-SUP-HDR | 2nd Level Chiller Room | CHW Supply Main Header Pressure | AI | Pressure Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0139 | AC | CHW Supply Main Header | CHW-SUP-HDR | 2nd Level Chiller Room | CHW Supply Main Header Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0140 | AC | CHW Return Main Header | CHW-RET-HDR | 2nd Level Chiller Room | CHW Return Main Header Pressure | AI | Pressure Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0141 | AC | CHW Return Main Header | CHW-RET-HDR | 2nd Level Chiller Room | CHW Return Main Header Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0142 | AC | CHW Bypass Header | CHW-DIFF | 2nd Level Chiller Room | CHW Differential Pressure | AI | Diff. Pressure Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0143 | AC | CHW Bypass Header | CHW-DIFF | 2nd Level Chiller Room | CHW Differential Temperature | AI | Diff. Pressure Sensor | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0144 | AC | CHW Bypass Header | CHW-DIFF | 2nd Level Chiller Room | Isolation Motorized Valve Status CHW Bypass | DI | Electric Valve Actuator | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0145 | AC | Condenser Water Header | CW-HDR | Roof Deck CT Area | Condenser Water Supply Header Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0146 | AC | Condenser Water Header | CW-HDR | Roof Deck CT Area | Condenser Water Return Header Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0147 | AC | Cooling Tower | CT-1 | Roof Deck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0148 | AC | Cooling Tower | CT-1 | Roof Deck | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0149 | AC | Cooling Tower | CT-1 | Roof Deck | Fan Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0150 | AC | Cooling Tower | CT-1 | Roof Deck | Level Alarm Low (CT Basin) | DI | Level Sensor / Electrode | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0151 | AC | Cooling Tower | CT-1 | Roof Deck | Level Alarm High (CT Basin) | DI | Level Sensor / Electrode | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0152 | AC | Cooling Tower | CT-1 | Roof Deck | Isolation Motorized Valve Status COW Return & Supply | DI | Electric Valve Actuator | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0153 | AC | Cooling Tower | CT-1 | Roof Deck | Blowdown Corrosion/Scale Monitoring | AI | pH Sensor / Conductivity Sensor | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0154 | AC | Cooling Tower | CT-1 | Roof Deck | Motorized Blowdown Valve Status | DI | Electric Valve Actuator | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0155 | AC | Cooling Tower | CT-1 | Roof Deck | Motorized Blowdown Valve Control | DO | Electric Valve Actuator | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0156 | AC | Cooling Tower | CT-2 | Roof Deck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0157 | AC | Cooling Tower | CT-2 | Roof Deck | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0158 | AC | Cooling Tower | CT-2 | Roof Deck | Fan Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0159 | AC | Cooling Tower | CT-2 | Roof Deck | Level Alarm Low (CT Basin) | DI | Level Sensor / Electrode | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0160 | AC | Cooling Tower | CT-2 | Roof Deck | Level Alarm High (CT Basin) | DI | Level Sensor / Electrode | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0161 | AC | Cooling Tower | CT-2 | Roof Deck | Isolation Motorized Valve Status COW Return & Supply | DI | Electric Valve Actuator | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0162 | AC | Cooling Tower | CT-2 | Roof Deck | Blowdown Corrosion/Scale Monitoring | AI | pH Sensor / Conductivity Sensor | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0163 | AC | Cooling Tower | CT-2 | Roof Deck | Motorized Blowdown Valve Status | DI | Electric Valve Actuator | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0164 | AC | Cooling Tower | CT-2 | Roof Deck | Motorized Blowdown Valve Control | DO | Electric Valve Actuator | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0165 | AC | Cooling Tower | CT-3 | Roof Deck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0166 | AC | Cooling Tower | CT-3 | Roof Deck | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0167 | AC | Cooling Tower | CT-3 | Roof Deck | Fan Start/Stop Command | DO | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0168 | AC | Cooling Tower | CT-3 | Roof Deck | Level Alarm Low (CT Basin) | DI | Level Sensor / Electrode | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0169 | AC | Cooling Tower | CT-3 | Roof Deck | Level Alarm High (CT Basin) | DI | Level Sensor / Electrode | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0170 | AC | Cooling Tower | CT-3 | Roof Deck | Isolation Motorized Valve Status COW Return & Supply | DI | Electric Valve Actuator | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0171 | AC | Cooling Tower | CT-3 | Roof Deck | Blowdown Corrosion/Scale Monitoring | AI | pH Sensor / Conductivity Sensor | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0172 | AC | Cooling Tower | CT-3 | Roof Deck | Motorized Blowdown Valve Status | DI | Electric Valve Actuator | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0173 | AC | Cooling Tower | CT-3 | Roof Deck | Motorized Blowdown Valve Control | DO | Electric Valve Actuator | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0174 | AC | Cooling Tower (Common) | CT-COMMON | Roof Deck | Outside Air Temperature Monitoring | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0175 | AC | Cooling Tower (Common) | CT-COMMON | Roof Deck | Outside Air Humidity Monitoring | AI | Humidity Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0176 | AC | Cooling Tower (Common) | CT-COMMON | Roof Deck | Water Temp Monitoring (Condenser Return Header) | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0177 | AC | Cooling Tower (Common) | CT-COMMON | Roof Deck | Water Temp Monitoring (Condenser Supply Header) | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0178 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Supply Steam Pressure | AI | Pressure Sensor | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0179 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Low Water Level | DI | Level Sensor | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0180 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | High Water Level | DI | Level Sensor | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0181 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Burner Power | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0182 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Small Fire Control Signal | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0183 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Big Fire Control Signal | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0184 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Waterfeed Pump Status | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0185 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Burner Status | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0186 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Burner Fire Running Status | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0187 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Blower Motor Status | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0188 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Fuel Oil Pump Status | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0189 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Motorized Valve Status Blowdown Water | DI | Electric Valve Actuator | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0190 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Motorized Valve Control Blowdown Water | DO | Electric Valve Actuator | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0191 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Feedwater Supply Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0192 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Fluegas Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0193 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Fluegas Oxygen Level | AI | Oxygen Sensor | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0194 | VENT | Steam Boiler | SB-1 | Lower Ground Boiler Room | Network drop (BACnet MS/TP — Burner Controller) | Network | Burner Controller gateway | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0195 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Supply Steam Pressure | AI | Pressure Sensor | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0196 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Low Water Level | DI | Level Sensor | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0197 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | High Water Level | DI | Level Sensor | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0198 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Burner Power | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0199 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Small Fire Control Signal | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0200 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Big Fire Control Signal | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0201 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Waterfeed Pump Status | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0202 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Burner Status | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0203 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Burner Fire Running Status | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0204 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Blower Motor Status | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0205 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Fuel Oil Pump Status | HLI | Burner Controller | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0206 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Motorized Valve Status Blowdown Water | DI | Electric Valve Actuator | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0207 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Motorized Valve Control Blowdown Water | DO | Electric Valve Actuator | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0208 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Feedwater Supply Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0209 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Fluegas Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0210 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Fluegas Oxygen Level | AI | Oxygen Sensor | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0211 | VENT | Steam Boiler | SB-2 | Lower Ground Boiler Room | Network drop (BACnet MS/TP — Burner Controller) | Network | Burner Controller gateway | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0212 | HWL | Calorifier (Hot Water Storage Tank) | HWT-LZ | Lower Ground HWL Room | Tank Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0213 | HWL | Calorifier (Hot Water Storage Tank) | HWT-HZ | Roof Deck HWL Area | Tank Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0214 | HWL | Hot Water Header Set | HWH-LZ | Lower Ground HWL Room | Hot Water Supply Header Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0215 | HWL | Hot Water Header Set | HWH-LZ | Lower Ground HWL Room | Make-Up Cold Water Header Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0216 | HWL | Hot Water Header Set | HWH-LZ | Lower Ground HWL Room | Hot Water Return Header Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0217 | HWL | Hot Water Header Set | HWH-HZ | Roof Deck HWL Area | Hot Water Supply Header Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0218 | HWL | Hot Water Header Set | HWH-HZ | Roof Deck HWL Area | Make-Up Cold Water Header Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0219 | HWL | Hot Water Header Set | HWH-HZ | Roof Deck HWL Area | Hot Water Return Header Temperature | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0220 | HWL | Heat Pump | HP-LZ | Lower Ground HWL Room | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0221 | HWL | Heat Pump | HP-LZ | Lower Ground HWL Room | Pump Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0222 | HWL | Heat Pump | HP-LZ | Lower Ground HWL Room | Pump Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0223 | HWL | Heat Pump | HP-HZ | Roof Deck HWL Area | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0224 | HWL | Heat Pump | HP-HZ | Roof Deck HWL Area | Pump Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0225 | HWL | Heat Pump | HP-HZ | Roof Deck HWL Area | Pump Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0226 | HWL | Recirculating Pump | RP-LZ | Lower Ground HWL Room | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0227 | HWL | Recirculating Pump | RP-LZ | Lower Ground HWL Room | Pump Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0228 | HWL | Recirculating Pump | RP-LZ | Lower Ground HWL Room | Pump Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0229 | HWL | Recirculating Pump | RP-HZ | Roof Deck HWL Area | Pump Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0230 | HWL | Recirculating Pump | RP-HZ | Roof Deck HWL Area | Pump Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0231 | HWL | Recirculating Pump | RP-HZ | Roof Deck HWL Area | Pump Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0232 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0233 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Flow Monitoring (Outside — Supply Air) | AI | Flow Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0234 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Humidity Monitoring (Outdoor — Supply Air) | AI | Humidity Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0235 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0236 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0237 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Recovery Wheel Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0238 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Recovery Wheel Motor Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0239 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Supply Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0240 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Supply Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0241 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Supply Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0242 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Supply Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0243 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Supply Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0244 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0245 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Humidity Monitoring (Indoor — Mixed Air) | AI | Humidity Sensor | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0246 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | CHWS / Cooling Coil Valve Status | AI | Electric Valve Actuator | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0247 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0248 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0249 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Humidity Monitoring (Indoor — Exhaust Air) | AI | Humidity Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0250 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Temperature Monitoring (Indoor — Exhaust Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0251 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Exhaust Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0252 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Exhaust Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0253 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Exhaust Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0254 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Exhaust Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0255 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Exhaust Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0256 | VENT | DOAS Unit | DOAS-RD.1 | Roof Deck | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0257 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0258 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Flow Monitoring (Outside — Supply Air) | AI | Flow Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0259 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Humidity Monitoring (Outdoor — Supply Air) | AI | Humidity Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0260 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0261 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0262 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Recovery Wheel Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0263 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Recovery Wheel Motor Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0264 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Supply Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0265 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Supply Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0266 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Supply Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0267 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Supply Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0268 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Supply Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0269 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0270 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Humidity Monitoring (Indoor — Mixed Air) | AI | Humidity Sensor | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0271 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | CHWS / Cooling Coil Valve Status | AI | Electric Valve Actuator | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0272 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0273 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0274 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Humidity Monitoring (Indoor — Exhaust Air) | AI | Humidity Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0275 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Temperature Monitoring (Indoor — Exhaust Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0276 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Exhaust Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0277 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Exhaust Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0278 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Exhaust Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0279 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Exhaust Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0280 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Exhaust Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0281 | VENT | DOAS Unit | DOAS-RD.2 | Roof Deck | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0282 | VENT | Precooled Air Handling Unit | PAHU-r.1 | Roof Deck | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0283 | VENT | Precooled Air Handling Unit | PAHU-r.1 | Roof Deck | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0284 | VENT | Precooled Air Handling Unit | PAHU-r.1 | Roof Deck | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0285 | VENT | Precooled Air Handling Unit | PAHU-r.1 | Roof Deck | Flow Monitoring (Outside — Supply Air) | AI | Flow Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0286 | VENT | Precooled Air Handling Unit | PAHU-r.1 | Roof Deck | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0287 | VENT | Precooled Air Handling Unit | PAHU-r.1 | Roof Deck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0288 | VENT | Precooled Air Handling Unit | PAHU-r.1 | Roof Deck | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0289 | VENT | Precooled Air Handling Unit | PAHU-r.1 | Roof Deck | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0290 | VENT | Precooled Air Handling Unit | PAHU-r.1 | Roof Deck | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0291 | VENT | Precooled Air Handling Unit | PAHU-r.1 | Roof Deck | Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0292 | VENT | Precooled Air Handling Unit | PAHU-r.1 | Roof Deck | Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0293 | VENT | Precooled Air Handling Unit | PAHU-r.1 | Roof Deck | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0294 | VENT | Precooled Air Handling Unit | PAHU-r.2 | Roof Deck | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0295 | VENT | Precooled Air Handling Unit | PAHU-r.2 | Roof Deck | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0296 | VENT | Precooled Air Handling Unit | PAHU-r.2 | Roof Deck | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0297 | VENT | Precooled Air Handling Unit | PAHU-r.2 | Roof Deck | Flow Monitoring (Outside — Supply Air) | AI | Flow Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0298 | VENT | Precooled Air Handling Unit | PAHU-r.2 | Roof Deck | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0299 | VENT | Precooled Air Handling Unit | PAHU-r.2 | Roof Deck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0300 | VENT | Precooled Air Handling Unit | PAHU-r.2 | Roof Deck | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0301 | VENT | Precooled Air Handling Unit | PAHU-r.2 | Roof Deck | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0302 | VENT | Precooled Air Handling Unit | PAHU-r.2 | Roof Deck | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0303 | VENT | Precooled Air Handling Unit | PAHU-r.2 | Roof Deck | Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0304 | VENT | Precooled Air Handling Unit | PAHU-r.2 | Roof Deck | Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0305 | VENT | Precooled Air Handling Unit | PAHU-r.2 | Roof Deck | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0306 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0307 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Flow Monitoring (Outside — Supply Air) | AI | Flow Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0308 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Humidity Monitoring (Outdoor — Supply Air) | AI | Humidity Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0309 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0310 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0311 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Recovery Wheel Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0312 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Recovery Wheel Motor Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0313 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Supply Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0314 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Supply Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0315 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Supply Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0316 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Supply Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0317 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Supply Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0318 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0319 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Humidity Monitoring (Indoor — Mixed Air) | AI | Humidity Sensor | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0320 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0321 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Carbon Dioxide (CO2) Sensor at Return Duct | AI | CO2 Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0322 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Carbon Monoxide (CO) Sensor at Return Duct (Casino) | AI | CO Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0323 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Exhaust Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0324 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Exhaust Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0325 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Exhaust Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0326 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Exhaust Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0327 | VENT | DOAS Unit (Casino — with CO/VOC) | DOAS-2M | 2nd Mezzanine (Casino) | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0328 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Indoor Return Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0329 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Indoor Return Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0330 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Indoor Return Air CO2 Level | AI | CO2 Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0331 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Temperature Monitoring (Indoor — Return Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0332 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0333 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0334 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0335 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0336 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0337 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0338 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0339 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0340 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0341 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Fan Control On/Off/Modulating (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0342 | AC | AHU (Chilled-Water-Served) | AHU-2M.1 | 2nd Mezzanine (Casino) | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0343 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Indoor Return Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0344 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Indoor Return Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0345 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Indoor Return Air CO2 Level | AI | CO2 Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0346 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Temperature Monitoring (Indoor — Return Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0347 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0348 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0349 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0350 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0351 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0352 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0353 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0354 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0355 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0356 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Fan Control On/Off/Modulating (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0357 | AC | AHU (Chilled-Water-Served) | AHU-2M.2 | 2nd Mezzanine (Casino) | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0358 | AC | Air Ionizer (Casino) | AIR-ION-2M.1 | 2nd Mezzanine (Casino) | VOC Monitoring (Return Duct) | AI | VOC Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0359 | AC | Air Ionizer (Casino) | AIR-ION-2M.1 | 2nd Mezzanine (Casino) | Air Ionizer Equipment Status | DI | Auxiliary Contact / Modbus | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0360 | AC | Air Ionizer (Casino) | AIR-ION-2M.1 | 2nd Mezzanine (Casino) | Air Ionizer Equipment Trip Status | DI | Auxiliary Contact / Modbus | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0361 | AC | Air Ionizer (Casino) | AIR-ION-2M.1 | 2nd Mezzanine (Casino) | Network drop (Modbus / BACnet MS-TP — Ionizer Controller) | Network | Ionizer Controller | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0362 | AC | Air Ionizer (Casino) | AIR-ION-2M.2 | 2nd Mezzanine (Casino) | VOC Monitoring (Return Duct) | AI | VOC Sensor | BMS Contractor |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0363 | AC | Air Ionizer (Casino) | AIR-ION-2M.2 | 2nd Mezzanine (Casino) | Air Ionizer Equipment Status | DI | Auxiliary Contact / Modbus | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0364 | AC | Air Ionizer (Casino) | AIR-ION-2M.2 | 2nd Mezzanine (Casino) | Air Ionizer Equipment Trip Status | DI | Auxiliary Contact / Modbus | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0365 | AC | Air Ionizer (Casino) | AIR-ION-2M.2 | 2nd Mezzanine (Casino) | Network drop (Modbus / BACnet MS-TP — Ionizer Controller) | Network | Ionizer Controller | Equipment Supplier |  | DDC-2M-CASINO | BMS-01/02 + MC Standards ME/PL
P-0366 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Indoor Return Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0367 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Indoor Return Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0368 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Indoor Return Air CO2 Level | AI | CO2 Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0369 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Temperature Monitoring (Indoor — Return Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0370 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0371 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0372 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0373 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0374 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0375 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0376 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0377 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0378 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0379 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Fan Control On/Off/Modulating (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0380 | AC | AHU (Chilled-Water-Served) | AHU-B.1 | 2nd Level BOH | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0381 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Indoor Return Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0382 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Indoor Return Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0383 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Indoor Return Air CO2 Level | AI | CO2 Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0384 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Temperature Monitoring (Indoor — Return Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0385 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0386 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0387 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0388 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0389 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0390 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0391 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0392 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0393 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0394 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Fan Control On/Off/Modulating (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0395 | AC | AHU (Chilled-Water-Served) | AHU-B.2 | 2nd Level BOH | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0396 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Indoor Return Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0397 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Indoor Return Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0398 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Indoor Return Air CO2 Level | AI | CO2 Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0399 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Temperature Monitoring (Indoor — Return Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0400 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0401 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0402 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0403 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0404 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0405 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0406 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0407 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0408 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0409 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Fan Control On/Off/Modulating (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0410 | AC | AHU (Chilled-Water-Served) | AHU-B.3 | 2nd Level BOH | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0411 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Indoor Return Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0412 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Indoor Return Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0413 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Indoor Return Air CO2 Level | AI | CO2 Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0414 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Temperature Monitoring (Indoor — Return Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0415 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0416 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0417 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0418 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0419 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0420 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0421 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0422 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0423 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0424 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Fan Control On/Off/Modulating (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0425 | AC | AHU (Chilled-Water-Served) | AHU-PF | 2nd Level Pre-Function | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0426 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Indoor Return Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0427 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Indoor Return Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0428 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Indoor Return Air CO2 Level | AI | CO2 Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0429 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Temperature Monitoring (Indoor — Return Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0430 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0431 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0432 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0433 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0434 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0435 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0436 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0437 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0438 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0439 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Fan Control On/Off/Modulating (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0440 | AC | AHU (Chilled-Water-Served) | AHU-EL | 2nd Level Executive Lounge | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0441 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Indoor Return Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0442 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Indoor Return Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0443 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Indoor Return Air CO2 Level | AI | CO2 Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0444 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Temperature Monitoring (Indoor — Return Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0445 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0446 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0447 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0448 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0449 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0450 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0451 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0452 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0453 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0454 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Fan Control On/Off/Modulating (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0455 | AC | AHU (Chilled-Water-Served) | AHU-FR2 | 2nd Level Function Room 2 | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0456 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Indoor Return Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0457 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Indoor Return Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0458 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Indoor Return Air CO2 Level | AI | CO2 Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0459 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Temperature Monitoring (Indoor — Return Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0460 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0461 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0462 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0463 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0464 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0465 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0466 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0467 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0468 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0469 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Fan Control On/Off/Modulating (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0470 | AC | AHU (Chilled-Water-Served) | AHU-FR3 | 2nd Level Function Room 3 | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0471 | VENT | Precooled Air Handling Unit | PAHU-B.1 | 2nd Level BOH | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0472 | VENT | Precooled Air Handling Unit | PAHU-B.1 | 2nd Level BOH | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0473 | VENT | Precooled Air Handling Unit | PAHU-B.1 | 2nd Level BOH | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0474 | VENT | Precooled Air Handling Unit | PAHU-B.1 | 2nd Level BOH | Flow Monitoring (Outside — Supply Air) | AI | Flow Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0475 | VENT | Precooled Air Handling Unit | PAHU-B.1 | 2nd Level BOH | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0476 | VENT | Precooled Air Handling Unit | PAHU-B.1 | 2nd Level BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0477 | VENT | Precooled Air Handling Unit | PAHU-B.1 | 2nd Level BOH | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0478 | VENT | Precooled Air Handling Unit | PAHU-B.1 | 2nd Level BOH | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0479 | VENT | Precooled Air Handling Unit | PAHU-B.1 | 2nd Level BOH | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0480 | VENT | Precooled Air Handling Unit | PAHU-B.1 | 2nd Level BOH | Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0481 | VENT | Precooled Air Handling Unit | PAHU-B.1 | 2nd Level BOH | Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0482 | VENT | Precooled Air Handling Unit | PAHU-B.1 | 2nd Level BOH | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0483 | VENT | Precooled Air Handling Unit | PAHU-B.2 | 2nd Level BOH | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0484 | VENT | Precooled Air Handling Unit | PAHU-B.2 | 2nd Level BOH | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0485 | VENT | Precooled Air Handling Unit | PAHU-B.2 | 2nd Level BOH | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0486 | VENT | Precooled Air Handling Unit | PAHU-B.2 | 2nd Level BOH | Flow Monitoring (Outside — Supply Air) | AI | Flow Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0487 | VENT | Precooled Air Handling Unit | PAHU-B.2 | 2nd Level BOH | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0488 | VENT | Precooled Air Handling Unit | PAHU-B.2 | 2nd Level BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0489 | VENT | Precooled Air Handling Unit | PAHU-B.2 | 2nd Level BOH | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0490 | VENT | Precooled Air Handling Unit | PAHU-B.2 | 2nd Level BOH | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0491 | VENT | Precooled Air Handling Unit | PAHU-B.2 | 2nd Level BOH | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0492 | VENT | Precooled Air Handling Unit | PAHU-B.2 | 2nd Level BOH | Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0493 | VENT | Precooled Air Handling Unit | PAHU-B.2 | 2nd Level BOH | Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0494 | VENT | Precooled Air Handling Unit | PAHU-B.2 | 2nd Level BOH | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0495 | VENT | Precooled Air Handling Unit | PAHU-B.3 | 2nd Level BOH | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0496 | VENT | Precooled Air Handling Unit | PAHU-B.3 | 2nd Level BOH | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0497 | VENT | Precooled Air Handling Unit | PAHU-B.3 | 2nd Level BOH | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0498 | VENT | Precooled Air Handling Unit | PAHU-B.3 | 2nd Level BOH | Flow Monitoring (Outside — Supply Air) | AI | Flow Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0499 | VENT | Precooled Air Handling Unit | PAHU-B.3 | 2nd Level BOH | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0500 | VENT | Precooled Air Handling Unit | PAHU-B.3 | 2nd Level BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0501 | VENT | Precooled Air Handling Unit | PAHU-B.3 | 2nd Level BOH | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0502 | VENT | Precooled Air Handling Unit | PAHU-B.3 | 2nd Level BOH | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0503 | VENT | Precooled Air Handling Unit | PAHU-B.3 | 2nd Level BOH | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0504 | VENT | Precooled Air Handling Unit | PAHU-B.3 | 2nd Level BOH | Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0505 | VENT | Precooled Air Handling Unit | PAHU-B.3 | 2nd Level BOH | Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0506 | VENT | Precooled Air Handling Unit | PAHU-B.3 | 2nd Level BOH | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0507 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Level Pre-Function | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0508 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Level Pre-Function | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0509 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Level Pre-Function | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0510 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Level Pre-Function | Flow Monitoring (Outside — Supply Air) | AI | Flow Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0511 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Level Pre-Function | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0512 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Level Pre-Function | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0513 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Level Pre-Function | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0514 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Level Pre-Function | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0515 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Level Pre-Function | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0516 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Level Pre-Function | Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0517 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Level Pre-Function | Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0518 | VENT | Precooled Air Handling Unit | PAHU-PF | 2nd Level Pre-Function | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0519 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Level Function Rooms | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0520 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Level Function Rooms | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0521 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Level Function Rooms | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0522 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Level Function Rooms | Flow Monitoring (Outside — Supply Air) | AI | Flow Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0523 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Level Function Rooms | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0524 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Level Function Rooms | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0525 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Level Function Rooms | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0526 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Level Function Rooms | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0527 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Level Function Rooms | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0528 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Level Function Rooms | Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0529 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Level Function Rooms | Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0530 | VENT | Precooled Air Handling Unit | PAHU-FR | 2nd Level Function Rooms | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0531 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Indoor Return Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0532 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Indoor Return Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0533 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Indoor Return Air CO2 Level | AI | CO2 Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0534 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Temperature Monitoring (Indoor — Return Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0535 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0536 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0537 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0538 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0539 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0540 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0541 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0542 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0543 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0544 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Fan Control On/Off/Modulating (HLI) | HLI | VFD | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0545 | AC | AHU (Chilled-Water-Served) | AHU-1.1 | Ground Floor BOH | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0546 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Indoor Return Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0547 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Indoor Return Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0548 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Indoor Return Air CO2 Level | AI | CO2 Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0549 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Temperature Monitoring (Indoor — Return Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0550 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0551 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0552 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0553 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0554 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0555 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0556 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0557 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0558 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0559 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Fan Control On/Off/Modulating (HLI) | HLI | VFD | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0560 | AC | AHU (Chilled-Water-Served) | AHU-1.2 | Ground Floor BOH | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0561 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Indoor Return Air Motorized Damper Status | AI | Damper Controller | ME Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0562 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Indoor Return Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | ME Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0563 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Indoor Return Air CO2 Level | AI | CO2 Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0564 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Temperature Monitoring (Indoor — Return Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0565 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Temperature Monitoring (Indoor — Mixed Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0566 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0567 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0568 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0569 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0570 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0571 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0572 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0573 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Fan Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0574 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Fan Control On/Off/Modulating (HLI) | HLI | VFD | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0575 | AC | AHU (Chilled-Water-Served) | AHU-1.3 | Ground Floor BOH | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0576 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Outdoor Supply Air Motorized Damper Status | AI | Damper Controller | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0577 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Outdoor Supply Air Motorized Damper Control (On/Off/Modulating) | AO | Damper Controller | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0578 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Temperature Monitoring (Outside — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0579 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Flow Monitoring (Outside — Supply Air) | AI | Flow Sensor | BMS Contractor |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0580 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | CHWS Valve Control (On/Off/Modulating) | AO | Electric Valve Actuator | ME Contractor |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0581 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0582 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0583 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0584 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Temperature Monitoring (Indoor — Supply Air) | AI | Temperature Sensor | BMS Contractor |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0585 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Variable Speed Monitoring (HLI) | HLI | VFD | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0586 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Fan Control (On/Off/Modulating) (HLI) | HLI | VFD | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0587 | VENT | Precooled Air Handling Unit | PAHU-0.1 | Basement | Network drop (BACnet MS/TP — VFD) | Network | VFD BACnet card | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0588 | VENT | Exhaust Fan (Toilet) | TEF-1.1 | GF Main Lobby Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0589 | VENT | Exhaust Fan (Toilet) | TEF-1.1 | GF Main Lobby Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0590 | VENT | Exhaust Fan (Toilet) | TEF-1.1 | GF Main Lobby Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0591 | VENT | Exhaust Fan (Toilet) | TEF-1.2 | GF Main Lobby Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0592 | VENT | Exhaust Fan (Toilet) | TEF-1.2 | GF Main Lobby Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0593 | VENT | Exhaust Fan (Toilet) | TEF-1.2 | GF Main Lobby Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0594 | VENT | Exhaust Fan (Toilet) | TEF-1.3 | GF Main Lobby Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0595 | VENT | Exhaust Fan (Toilet) | TEF-1.3 | GF Main Lobby Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0596 | VENT | Exhaust Fan (Toilet) | TEF-1.3 | GF Main Lobby Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0597 | VENT | Exhaust Fan (Toilet) | TEF-1.4 | GF Main Lobby Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0598 | VENT | Exhaust Fan (Toilet) | TEF-1.4 | GF Main Lobby Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0599 | VENT | Exhaust Fan (Toilet) | TEF-1.4 | GF Main Lobby Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0600 | VENT | Exhaust Fan (Toilet) | TEF-2.1 | 2nd Floor Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0601 | VENT | Exhaust Fan (Toilet) | TEF-2.1 | 2nd Floor Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0602 | VENT | Exhaust Fan (Toilet) | TEF-2.1 | 2nd Floor Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0603 | VENT | Exhaust Fan (Toilet) | TEF-2.2 | 2nd Floor Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0604 | VENT | Exhaust Fan (Toilet) | TEF-2.2 | 2nd Floor Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0605 | VENT | Exhaust Fan (Toilet) | TEF-2.2 | 2nd Floor Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0606 | VENT | Exhaust Fan (Toilet) | TEF-2B.3 | 2nd Floor BOH Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0607 | VENT | Exhaust Fan (Toilet) | TEF-2B.3 | 2nd Floor BOH Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0608 | VENT | Exhaust Fan (Toilet) | TEF-2B.3 | 2nd Floor BOH Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0609 | VENT | Exhaust Fan (General) | EF-2B.1 | 2nd Floor BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0610 | VENT | Exhaust Fan (General) | EF-2B.1 | 2nd Floor BOH | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0611 | VENT | Exhaust Fan (General) | EF-2B.1 | 2nd Floor BOH | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0612 | VENT | Exhaust Fan (General) | EF-2B.2 | 2nd Floor BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0613 | VENT | Exhaust Fan (General) | EF-2B.2 | 2nd Floor BOH | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0614 | VENT | Exhaust Fan (General) | EF-2B.2 | 2nd Floor BOH | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0615 | VENT | Exhaust Fan (General) | EF-GS.1 | 2nd Floor General Service | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0616 | VENT | Exhaust Fan (General) | EF-GS.1 | 2nd Floor General Service | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0617 | VENT | Exhaust Fan (General) | EF-GS.1 | 2nd Floor General Service | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0618 | VENT | Exhaust Fan (General) | EF-GS.2 | 2nd Floor General Service | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0619 | VENT | Exhaust Fan (General) | EF-GS.2 | 2nd Floor General Service | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0620 | VENT | Exhaust Fan (General) | EF-GS.2 | 2nd Floor General Service | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0621 | VENT | Exhaust Fan (General) | EF-2.1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0622 | VENT | Exhaust Fan (General) | EF-2.1 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0623 | VENT | Exhaust Fan (General) | EF-2.1 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0624 | VENT | Exhaust Fan (General) | EF-2.2 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0625 | VENT | Exhaust Fan (General) | EF-2.2 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0626 | VENT | Exhaust Fan (General) | EF-2.2 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0627 | VENT | Exhaust Fan (General) | EF-2.3 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0628 | VENT | Exhaust Fan (General) | EF-2.3 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0629 | VENT | Exhaust Fan (General) | EF-2.3 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0630 | VENT | Exhaust Fan (General) | EF-2.4 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0631 | VENT | Exhaust Fan (General) | EF-2.4 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0632 | VENT | Exhaust Fan (General) | EF-2.4 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0633 | VENT | Exhaust Fan (General) | EF-OHRv2 | 2nd Floor OHR | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0634 | VENT | Exhaust Fan (General) | EF-OHRv2 | 2nd Floor OHR | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0635 | VENT | Exhaust Fan (General) | EF-OHRv2 | 2nd Floor OHR | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0636 | VENT | Exhaust Fan (Toilet) | TEF-3A.1 | 3rd Floor Amenity Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0637 | VENT | Exhaust Fan (Toilet) | TEF-3A.1 | 3rd Floor Amenity Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0638 | VENT | Exhaust Fan (Toilet) | TEF-3A.1 | 3rd Floor Amenity Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0639 | VENT | Exhaust Fan (Toilet) | TEF-3A.2 | 3rd Floor Amenity Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0640 | VENT | Exhaust Fan (Toilet) | TEF-3A.2 | 3rd Floor Amenity Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0641 | VENT | Exhaust Fan (Toilet) | TEF-3A.2 | 3rd Floor Amenity Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0642 | VENT | Exhaust Fan (Toilet) | TEF-3B | 3rd Floor Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0643 | VENT | Exhaust Fan (Toilet) | TEF-3B | 3rd Floor Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0644 | VENT | Exhaust Fan (Toilet) | TEF-3B | 3rd Floor Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0645 | VENT | Exhaust Fan (Toilet) | TEF-3C.1 | 3rd Floor Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0646 | VENT | Exhaust Fan (Toilet) | TEF-3C.1 | 3rd Floor Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0647 | VENT | Exhaust Fan (Toilet) | TEF-3C.1 | 3rd Floor Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0648 | VENT | Exhaust Fan (Toilet) | TEF-3C.2 | 3rd Floor Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0649 | VENT | Exhaust Fan (Toilet) | TEF-3C.2 | 3rd Floor Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0650 | VENT | Exhaust Fan (Toilet) | TEF-3C.2 | 3rd Floor Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0651 | VENT | Exhaust Fan (Toilet) | TEF-30.20 | 3rd Floor Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0652 | VENT | Exhaust Fan (Toilet) | TEF-30.20 | 3rd Floor Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0653 | VENT | Exhaust Fan (Toilet) | TEF-30.20 | 3rd Floor Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0654 | VENT | Exhaust Fan (General) | EF-3.1 | 3rd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0655 | VENT | Exhaust Fan (General) | EF-3.1 | 3rd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0656 | VENT | Exhaust Fan (General) | EF-3.1 | 3rd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0657 | VENT | Exhaust Fan (General) | EF-3.2 | 3rd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0658 | VENT | Exhaust Fan (General) | EF-3.2 | 3rd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0659 | VENT | Exhaust Fan (General) | EF-3.2 | 3rd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0660 | VENT | Exhaust Fan (General) | EF-3.3 | 3rd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0661 | VENT | Exhaust Fan (General) | EF-3.3 | 3rd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0662 | VENT | Exhaust Fan (General) | EF-3.3 | 3rd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0663 | VENT | Exhaust Fan (General) | EF-3.4 | 3rd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0664 | VENT | Exhaust Fan (General) | EF-3.4 | 3rd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0665 | VENT | Exhaust Fan (General) | EF-3.4 | 3rd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0666 | VENT | Exhaust Fan (General) | EF-3B-G | 3rd Floor BOH | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0667 | VENT | Exhaust Fan (General) | EF-3B-G | 3rd Floor BOH | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0668 | VENT | Exhaust Fan (General) | EF-3B-G | 3rd Floor BOH | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0669 | VENT | Exhaust Fan (General) | EF-3C.1-G | 3rd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0670 | VENT | Exhaust Fan (General) | EF-3C.1-G | 3rd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0671 | VENT | Exhaust Fan (General) | EF-3C.1-G | 3rd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-3F | BMS-01/02 + MC Standards ME/PL
P-0672 | VENT | Exhaust Fan (Toilet) | TEF-B.1 | Basement Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0673 | VENT | Exhaust Fan (Toilet) | TEF-B.1 | Basement Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0674 | VENT | Exhaust Fan (Toilet) | TEF-B.1 | Basement Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0675 | VENT | Exhaust Fan (Toilet) | TEF-B.2 | Basement Toilet | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0676 | VENT | Exhaust Fan (Toilet) | TEF-B.2 | Basement Toilet | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0677 | VENT | Exhaust Fan (Toilet) | TEF-B.2 | Basement Toilet | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0678 | VENT | Exhaust Fan (General) | EF-B.1 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0679 | VENT | Exhaust Fan (General) | EF-B.1 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0680 | VENT | Exhaust Fan (General) | EF-B.1 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0681 | VENT | Exhaust Fan (General) | EF-B.2 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0682 | VENT | Exhaust Fan (General) | EF-B.2 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0683 | VENT | Exhaust Fan (General) | EF-B.2 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0684 | VENT | Exhaust Fan (General) | EF-BS.1 | Basement Service | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0685 | VENT | Exhaust Fan (General) | EF-BS.1 | Basement Service | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0686 | VENT | Exhaust Fan (General) | EF-BS.1 | Basement Service | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0687 | VENT | Exhaust Fan (General) | EF-BS.2 | Basement Service | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0688 | VENT | Exhaust Fan (General) | EF-BS.2 | Basement Service | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0689 | VENT | Exhaust Fan (General) | EF-BS.2 | Basement Service | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0690 | VENT | Exhaust Fan (General) | EF-GL.1 | Basement Garbage Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0691 | VENT | Exhaust Fan (General) | EF-GL.1 | Basement Garbage Lobby | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0692 | VENT | Exhaust Fan (General) | EF-GL.1 | Basement Garbage Lobby | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0693 | VENT | Exhaust Fan (General) | EF-GL.2 | Basement Garbage Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0694 | VENT | Exhaust Fan (General) | EF-GL.2 | Basement Garbage Lobby | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0695 | VENT | Exhaust Fan (General) | EF-GL.2 | Basement Garbage Lobby | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0696 | VENT | Exhaust Fan (General) | EF-FOST.1 | Basement FOST Room | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0697 | VENT | Exhaust Fan (General) | EF-FOST.1 | Basement FOST Room | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0698 | VENT | Exhaust Fan (General) | EF-FOST.1 | Basement FOST Room | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0699 | VENT | Exhaust Fan (General) | EF-BR.1 | Basement Battery Room | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0700 | VENT | Exhaust Fan (General) | EF-BR.1 | Basement Battery Room | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0701 | VENT | Exhaust Fan (General) | EF-BR.1 | Basement Battery Room | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0702 | VENT | Exhaust Fan (General) | EF-BR.2 | Basement Battery Room | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0703 | VENT | Exhaust Fan (General) | EF-BR.2 | Basement Battery Room | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0704 | VENT | Exhaust Fan (General) | EF-BR.2 | Basement Battery Room | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0705 | VENT | Exhaust Fan (General) | EF-WS.1 | Basement Wash Service | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0706 | VENT | Exhaust Fan (General) | EF-WS.1 | Basement Wash Service | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0707 | VENT | Exhaust Fan (General) | EF-WS.1 | Basement Wash Service | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0708 | VENT | Exhaust Fan (General) | EF-MP.1 | Basement Mech / Pump | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0709 | VENT | Exhaust Fan (General) | EF-MP.1 | Basement Mech / Pump | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0710 | VENT | Exhaust Fan (General) | EF-MP.1 | Basement Mech / Pump | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0711 | VENT | Exhaust Fan (General) | EF-PR.1 | Basement Pump Room | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0712 | VENT | Exhaust Fan (General) | EF-PR.1 | Basement Pump Room | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0713 | VENT | Exhaust Fan (General) | EF-PR.1 | Basement Pump Room | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0714 | VENT | Exhaust Fan (General) | EF-PR.3 | Basement Pump Room | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0715 | VENT | Exhaust Fan (General) | EF-PR.3 | Basement Pump Room | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0716 | VENT | Exhaust Fan (General) | EF-PR.3 | Basement Pump Room | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0717 | VENT | Exhaust Fan (General) | EF-MFR.1 | Basement Main Fire Riser | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0718 | VENT | Exhaust Fan (General) | EF-MFR.1 | Basement Main Fire Riser | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0719 | VENT | Exhaust Fan (General) | EF-MFR.1 | Basement Main Fire Riser | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-B1-BOH | BMS-01/02 + MC Standards ME/PL
P-0720 | VENT | Exhaust Fan (General) | EF-RD.1 | Roof Deck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0721 | VENT | Exhaust Fan (General) | EF-RD.1 | Roof Deck | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0722 | VENT | Exhaust Fan (General) | EF-RD.1 | Roof Deck | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0723 | VENT | Exhaust Fan (General) | EF-RO.2 | Roof Deck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0724 | VENT | Exhaust Fan (General) | EF-RO.2 | Roof Deck | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0725 | VENT | Exhaust Fan (General) | EF-RO.2 | Roof Deck | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0726 | VENT | Exhaust Fan (General) | EF-1 | Roof Deck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0727 | VENT | Exhaust Fan (General) | EF-1 | Roof Deck | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0728 | VENT | Exhaust Fan (General) | EF-1 | Roof Deck | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier |  | DDC-RD-PLANT | BMS-01/02 + MC Standards ME/PL
P-0729 | EL | Multifunction Power Meter (Main) | MPM-MAIN | Lower Ground Main Switchroom | Multifunction power meter — voltage / current / kW / kWh / power factor / harmonics | HLI | Multifunction Power Meter | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0730 | EL | Multifunction Power Meter (Main) | MPM-MAIN | Lower Ground Main Switchroom | Network drop (Modbus TCP — Power Meter) | Network | Multifunction Power Meter | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0731 | EL | Multifunction Power Meter (Feeder) | MPM-CHILLER | 2nd Level Chiller MCC | Multifunction power meter — voltage / current / kW / kWh / power factor | HLI | Multifunction Power Meter | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0732 | EL | Multifunction Power Meter (Feeder) | MPM-CHILLER | 2nd Level Chiller MCC | Network drop (Modbus TCP — Power Meter) | Network | Multifunction Power Meter | BMS Contractor |  | DDC-2F-CHILLER | BMS-01/02 + MC Standards ME/PL
P-0733 | EL | Multifunction Power Meter (Feeder) | MPM-AHU-2F | 2nd Level AHU MCC | Multifunction power meter — voltage / current / kW / kWh / power factor | HLI | Multifunction Power Meter | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0734 | EL | Multifunction Power Meter (Feeder) | MPM-AHU-2F | 2nd Level AHU MCC | Network drop (Modbus TCP — Power Meter) | Network | Multifunction Power Meter | BMS Contractor |  | DDC-2F-BOH | BMS-01/02 + MC Standards ME/PL
P-0735 | EL | Multifunction Power Meter (Feeder) | MPM-AHU-GF | Ground Floor AHU MCC | Multifunction power meter — voltage / current / kW / kWh / power factor | HLI | Multifunction Power Meter | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0736 | EL | Multifunction Power Meter (Feeder) | MPM-AHU-GF | Ground Floor AHU MCC | Network drop (Modbus TCP — Power Meter) | Network | Multifunction Power Meter | BMS Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0737 | EL | Multifunction Power Meter (Feeder) | MPM-LIGHT-A | Lower Ground Lighting Panel A | Multifunction power meter — voltage / current / kW / kWh / power factor | HLI | Multifunction Power Meter | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0738 | EL | Multifunction Power Meter (Feeder) | MPM-LIGHT-A | Lower Ground Lighting Panel A | Network drop (Modbus TCP — Power Meter) | Network | Multifunction Power Meter | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0739 | EL | Multifunction Power Meter (Feeder) | MPM-LIGHT-B | Lower Ground Lighting Panel B | Multifunction power meter — voltage / current / kW / kWh / power factor | HLI | Multifunction Power Meter | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0740 | EL | Multifunction Power Meter (Feeder) | MPM-LIGHT-B | Lower Ground Lighting Panel B | Network drop (Modbus TCP — Power Meter) | Network | Multifunction Power Meter | BMS Contractor |  | DDC-LG-PLANT | BMS-01/02 + MC Standards ME/PL
P-0741 | FDAS | FACP Gateway | FACP-GW | Ground Floor Fire Command Center | Fire Alarm Common Alarm | HLI | FACP BACnet Gateway | EE Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0742 | FDAS | FACP Gateway | FACP-GW | Ground Floor Fire Command Center | Fire Alarm Common Trouble | HLI | FACP BACnet Gateway | EE Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0743 | FDAS | FACP Gateway | FACP-GW | Ground Floor Fire Command Center | Fire Alarm System Status | HLI | FACP BACnet Gateway | EE Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL
P-0744 | FDAS | FACP Gateway | FACP-GW | Ground Floor Fire Command Center | Network drop (BACnet/IP — FACP Gateway) | Network | FACP BACnet Gateway | EE Contractor |  | DDC-GF-BOH | BMS-01/02 + MC Standards ME/PL