## Summary
A2 — Equipment Takeoff Summary
Total instances | 109
By equipment class
Exhaust Fan (General) | 32
Exhaust Fan (Toilet) | 15
AHU (Chilled-Water-Served) | 12
Precooled Air Handling Unit | 8
Multifunction Power Meter (Feeder) | 5
Chiller (Package Water-Cooled) | 3
Condenser Water Pump | 3
Cooling Tower | 3
Secondary CHW Pump | 3
Air Ionizer (Casino) | 2
DOAS Unit | 2
Heat Pump | 2
Hot Water Header Set | 2
Calorifier (Hot Water Storage Tank) | 2
Primary CHW Pump | 2
Recirculating Pump | 2
Steam Boiler | 2
CHW Bypass Header | 1
CHW Return Main Header | 1
CHW Supply Main Header | 1
Cooling Tower (Common) | 1
Condenser Water Header | 1
DOAS Unit (Casino — with CO/VOC) | 1
FACP Gateway | 1
Multifunction Power Meter (Main) | 1
Primary CHW Pump (Standby) | 1
By location
2nd Level Chiller Room | 15
Roof Deck | 11
2nd Level BOH | 6
2nd Mezzanine (Casino) | 5
3rd Floor | 5
2nd Floor | 4
Roof Deck HWL Area | 4
Lower Ground HWL Room | 4
GF Main Lobby Toilet | 4
3rd Floor Toilet | 4
Ground Floor BOH | 3
Basement | 3
2nd Level Pre-Function | 2
2nd Floor BOH | 2
Basement Battery Room | 2
Basement Service | 2
Basement Garbage Lobby | 2
2nd Floor General Service | 2
Basement Pump Room | 2
Lower Ground Boiler Room | 2
2nd Floor Toilet | 2
3rd Floor Amenity Toilet | 2
Basement Toilet | 2
2nd Level Executive Lounge | 1
2nd Level Function Room 2 | 1
2nd Level Function Room 3 | 1
Roof Deck CT Area | 1
3rd Floor BOH | 1
Basement FOST Room | 1
Basement Main Fire Riser | 1
Basement Mech / Pump | 1
2nd Floor OHR | 1
Basement Wash Service | 1
Ground Floor Fire Command Center | 1
2nd Level AHU MCC | 1
Ground Floor AHU MCC | 1
2nd Level Chiller MCC | 1
Lower Ground Lighting Panel A | 1
Lower Ground Lighting Panel B | 1
Lower Ground Main Switchroom | 1
2nd Level Function Rooms | 1
2nd Floor BOH Toilet | 1
By panel
DDC-2F-BOH | 25
DDC-B1-BOH | 17
DDC-2F-CHILLER | 16
DDC-RD-PLANT | 16
DDC-3F | 12
DDC-GF-BOH | 9
DDC-LG-PLANT | 9
DDC-2M-CASINO | 5

## Equipment Takeoff
ID | Equipment Class | Quantity | Location | System | Panel | Primary C/O | Physical I/O | HLI Subpoints | Network Drops | Total I/O | Make/Model Assumed | Network Type | Typical Supplier | Notes
AHU-1.1 | AHU (Chilled-Water-Served) | 1 | Ground Floor BOH | AC | DDC-GF-BOH | Equipment Supplier | 12 | 2 | 1 | 15 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-1.2 | AHU (Chilled-Water-Served) | 1 | Ground Floor BOH | AC | DDC-GF-BOH | Equipment Supplier | 12 | 2 | 1 | 15 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-1.3 | AHU (Chilled-Water-Served) | 1 | Ground Floor BOH | AC | DDC-GF-BOH | Equipment Supplier | 12 | 2 | 1 | 15 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-2M.1 | AHU (Chilled-Water-Served) | 1 | 2nd Mezzanine (Casino) | AC | DDC-2M-CASINO | Equipment Supplier | 12 | 2 | 1 | 15 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-2M.2 | AHU (Chilled-Water-Served) | 1 | 2nd Mezzanine (Casino) | AC | DDC-2M-CASINO | Equipment Supplier | 12 | 2 | 1 | 15 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-B.1 | AHU (Chilled-Water-Served) | 1 | 2nd Level BOH | AC | DDC-2F-BOH | Equipment Supplier | 12 | 2 | 1 | 15 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-B.2 | AHU (Chilled-Water-Served) | 1 | 2nd Level BOH | AC | DDC-2F-BOH | Equipment Supplier | 12 | 2 | 1 | 15 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-B.3 | AHU (Chilled-Water-Served) | 1 | 2nd Level BOH | AC | DDC-2F-BOH | Equipment Supplier | 12 | 2 | 1 | 15 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-EL | AHU (Chilled-Water-Served) | 1 | 2nd Level Executive Lounge | AC | DDC-2F-BOH | Equipment Supplier | 12 | 2 | 1 | 15 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-FR2 | AHU (Chilled-Water-Served) | 1 | 2nd Level Function Room 2 | AC | DDC-2F-BOH | Equipment Supplier | 12 | 2 | 1 | 15 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-FR3 | AHU (Chilled-Water-Served) | 1 | 2nd Level Function Room 3 | AC | DDC-2F-BOH | Equipment Supplier | 12 | 2 | 1 | 15 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AHU-PF | AHU (Chilled-Water-Served) | 1 | 2nd Level Pre-Function | AC | DDC-2F-BOH | Equipment Supplier | 12 | 2 | 1 | 15 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
AIR-ION-2M.1 | Air Ionizer (Casino) | 1 | 2nd Mezzanine (Casino) | AC | DDC-2M-CASINO | Equipment Supplier | 3 | 0 | 1 | 4 | (class default not defined — add to equipment-class-defaults.yaml) | TBD | TBD
AIR-ION-2M.2 | Air Ionizer (Casino) | 1 | 2nd Mezzanine (Casino) | AC | DDC-2M-CASINO | Equipment Supplier | 3 | 0 | 1 | 4 | (class default not defined — add to equipment-class-defaults.yaml) | TBD | TBD
CH-1 | Chiller (Package Water-Cooled) | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | Equipment Supplier | 9 | 18 | 1 | 28 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CH-2 | Chiller (Package Water-Cooled) | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | Equipment Supplier | 9 | 18 | 1 | 28 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CH-3 | Chiller (Package Water-Cooled) | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | Equipment Supplier | 9 | 18 | 1 | 28 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CHW-DIFF | CHW Bypass Header | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | BMS Contractor | 3 | 0 | 0 | 3 | BMS dP/dT sensors + motorized bypass valve (BMS-supplied) | Hardwired | BMS contractor | BMS controls bypass valve to maintain CHW differential.
CHW-RET-HDR | CHW Return Main Header | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | BMS Contractor | 2 | 0 | 0 | 2 | BMS T+P sensors on CHW return manifold | Hardwired | BMS contractor | Field instrumentation only.
CHW-SUP-HDR | CHW Supply Main Header | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | BMS Contractor | 2 | 0 | 0 | 2 | BMS T+P sensors on CHW supply manifold | Hardwired | BMS contractor | Field instrumentation only.
COWP-1 | Condenser Water Pump | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | Equipment Supplier | 4 | 0 | 0 | 4 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
COWP-2 | Condenser Water Pump | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | Equipment Supplier | 4 | 0 | 0 | 4 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
COWP-3 | Condenser Water Pump | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | Equipment Supplier | 4 | 0 | 0 | 4 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
CT-1 | Cooling Tower | 1 | Roof Deck | AC | DDC-RD-PLANT | BMS Contractor | 9 | 0 | 0 | 9 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-2 | Cooling Tower | 1 | Roof Deck | AC | DDC-RD-PLANT | BMS Contractor | 9 | 0 | 0 | 9 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-3 | Cooling Tower | 1 | Roof Deck | AC | DDC-RD-PLANT | BMS Contractor | 9 | 0 | 0 | 9 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-COMMON | Cooling Tower (Common) | 1 | Roof Deck | AC | DDC-RD-PLANT | BMS Contractor | 4 | 0 | 0 | 4 | Common BMS sensors at cooling tower area (OA T/RH, condenser headers) | Hardwired | BMS contractor | Field instrumentation only — no equipment per se.
CW-HDR | Condenser Water Header | 1 | Roof Deck CT Area | AC | DDC-RD-PLANT | BMS Contractor | 2 | 0 | 0 | 2 | BMS T sensors on condenser water headers at roofdeck | Hardwired | BMS contractor | Field instrumentation only.
DOAS-2M | DOAS Unit (Casino — with CO/VOC) | 1 | 2nd Mezzanine (Casino) | VENT | DDC-2M-CASINO | Equipment Supplier | 17 | 4 | 1 | 22 | (class default not defined — add to equipment-class-defaults.yaml) | TBD | TBD
DOAS-RD.1 | DOAS Unit | 1 | Roof Deck | VENT | DDC-RD-PLANT | Equipment Supplier | 20 | 4 | 1 | 25 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
DOAS-RD.2 | DOAS Unit | 1 | Roof Deck | VENT | DDC-RD-PLANT | Equipment Supplier | 20 | 4 | 1 | 25 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
EF-1 | Exhaust Fan (General) | 1 | Roof Deck | VENT | DDC-RD-PLANT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2.1 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | DDC-2F-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2.2 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | DDC-2F-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2.3 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | DDC-2F-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2.4 | Exhaust Fan (General) | 1 | 2nd Floor | VENT | DDC-2F-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2B.1 | Exhaust Fan (General) | 1 | 2nd Floor BOH | VENT | DDC-2F-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2B.2 | Exhaust Fan (General) | 1 | 2nd Floor BOH | VENT | DDC-2F-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-3.1 | Exhaust Fan (General) | 1 | 3rd Floor | VENT | DDC-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-3.2 | Exhaust Fan (General) | 1 | 3rd Floor | VENT | DDC-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-3.3 | Exhaust Fan (General) | 1 | 3rd Floor | VENT | DDC-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-3.4 | Exhaust Fan (General) | 1 | 3rd Floor | VENT | DDC-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-3B-G | Exhaust Fan (General) | 1 | 3rd Floor BOH | VENT | DDC-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-3C.1-G | Exhaust Fan (General) | 1 | 3rd Floor | VENT | DDC-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-B.1 | Exhaust Fan (General) | 1 | Basement | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-B.2 | Exhaust Fan (General) | 1 | Basement | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-BR.1 | Exhaust Fan (General) | 1 | Basement Battery Room | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-BR.2 | Exhaust Fan (General) | 1 | Basement Battery Room | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-BS.1 | Exhaust Fan (General) | 1 | Basement Service | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-BS.2 | Exhaust Fan (General) | 1 | Basement Service | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-FOST.1 | Exhaust Fan (General) | 1 | Basement FOST Room | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-GL.1 | Exhaust Fan (General) | 1 | Basement Garbage Lobby | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-GL.2 | Exhaust Fan (General) | 1 | Basement Garbage Lobby | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-GS.1 | Exhaust Fan (General) | 1 | 2nd Floor General Service | VENT | DDC-2F-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-GS.2 | Exhaust Fan (General) | 1 | 2nd Floor General Service | VENT | DDC-2F-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-MFR.1 | Exhaust Fan (General) | 1 | Basement Main Fire Riser | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-MP.1 | Exhaust Fan (General) | 1 | Basement Mech / Pump | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-OHRv2 | Exhaust Fan (General) | 1 | 2nd Floor OHR | VENT | DDC-2F-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-PR.1 | Exhaust Fan (General) | 1 | Basement Pump Room | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-PR.3 | Exhaust Fan (General) | 1 | Basement Pump Room | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-RD.1 | Exhaust Fan (General) | 1 | Roof Deck | VENT | DDC-RD-PLANT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-RO.2 | Exhaust Fan (General) | 1 | Roof Deck | VENT | DDC-RD-PLANT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-WS.1 | Exhaust Fan (General) | 1 | Basement Wash Service | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
FACP-GW | FACP Gateway | 1 | Ground Floor Fire Command Center | FDAS | DDC-GF-BOH | EE Contractor | 0 | 3 | 1 | 4 | (class default not defined — add to equipment-class-defaults.yaml) | TBD | TBD
HP-HZ | Heat Pump | 1 | Roof Deck HWL Area | HWL | DDC-RD-PLANT | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-LZ | Heat Pump | 1 | Lower Ground HWL Room | HWL | DDC-LG-PLANT | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HWH-HZ | Hot Water Header Set | 1 | Roof Deck HWL Area | HWL | DDC-RD-PLANT | BMS Contractor | 3 | 0 | 0 | 3 | Hot water supply/return manifolds with BMS T sensors and make-up cold water T sensor | Hardwired | BMS contractor | Field instrumentation on existing piping.
HWH-LZ | Hot Water Header Set | 1 | Lower Ground HWL Room | HWL | DDC-LG-PLANT | BMS Contractor | 3 | 0 | 0 | 3 | Hot water supply/return manifolds with BMS T sensors and make-up cold water T sensor | Hardwired | BMS contractor | Field instrumentation on existing piping.
HWT-HZ | Calorifier (Hot Water Storage Tank) | 1 | Roof Deck HWL Area | HWL | DDC-RD-PLANT | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-LZ | Calorifier (Hot Water Storage Tank) | 1 | Lower Ground HWL Room | HWL | DDC-LG-PLANT | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
MPM-AHU-2F | Multifunction Power Meter (Feeder) | 1 | 2nd Level AHU MCC | EL | DDC-2F-BOH | BMS Contractor | 0 | 1 | 1 | 2 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MPM-AHU-GF | Multifunction Power Meter (Feeder) | 1 | Ground Floor AHU MCC | EL | DDC-GF-BOH | BMS Contractor | 0 | 1 | 1 | 2 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MPM-CHILLER | Multifunction Power Meter (Feeder) | 1 | 2nd Level Chiller MCC | EL | DDC-2F-CHILLER | BMS Contractor | 0 | 1 | 1 | 2 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MPM-LIGHT-A | Multifunction Power Meter (Feeder) | 1 | Lower Ground Lighting Panel A | EL | DDC-LG-PLANT | BMS Contractor | 0 | 1 | 1 | 2 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MPM-LIGHT-B | Multifunction Power Meter (Feeder) | 1 | Lower Ground Lighting Panel B | EL | DDC-LG-PLANT | BMS Contractor | 0 | 1 | 1 | 2 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MPM-MAIN | Multifunction Power Meter (Main) | 1 | Lower Ground Main Switchroom | EL | DDC-LG-PLANT | BMS Contractor | 0 | 1 | 1 | 2 | Multifunction power meter with Modbus output (Schneider PM-series, ABB M2M, Siemens SENTRON), main switchgear class | Modbus RTU/TCP | BMS contractor | Mounted in main switchgear or on dedicated BMS-side panel.
PAHU-0.1 | Precooled Air Handling Unit | 1 | Basement | VENT | DDC-B1-BOH | Equipment Supplier | 9 | 2 | 1 | 12 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-B.1 | Precooled Air Handling Unit | 1 | 2nd Level BOH | VENT | DDC-2F-BOH | Equipment Supplier | 9 | 2 | 1 | 12 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-B.2 | Precooled Air Handling Unit | 1 | 2nd Level BOH | VENT | DDC-2F-BOH | Equipment Supplier | 9 | 2 | 1 | 12 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-B.3 | Precooled Air Handling Unit | 1 | 2nd Level BOH | VENT | DDC-2F-BOH | Equipment Supplier | 9 | 2 | 1 | 12 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-FR | Precooled Air Handling Unit | 1 | 2nd Level Function Rooms | VENT | DDC-2F-BOH | Equipment Supplier | 9 | 2 | 1 | 12 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-PF | Precooled Air Handling Unit | 1 | 2nd Level Pre-Function | VENT | DDC-2F-BOH | Equipment Supplier | 9 | 2 | 1 | 12 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-r.1 | Precooled Air Handling Unit | 1 | Roof Deck | VENT | DDC-RD-PLANT | Equipment Supplier | 9 | 2 | 1 | 12 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-r.2 | Precooled Air Handling Unit | 1 | Roof Deck | VENT | DDC-RD-PLANT | Equipment Supplier | 9 | 2 | 1 | 12 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PCHWP-1 | Primary CHW Pump | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | Equipment Supplier | 5 | 2 | 1 | 8 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
PCHWP-2 | Primary CHW Pump | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | Equipment Supplier | 5 | 2 | 1 | 8 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
PCHWP-3 | Primary CHW Pump (Standby) | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | Equipment Supplier | 4 | 0 | 0 | 4 | Same as Primary CHW Pump (1 standby for N+1 redundancy) | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | Standby unit per A-CHW-001.
RP-HZ | Recirculating Pump | 1 | Roof Deck HWL Area | HWL | DDC-RD-PLANT | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-LZ | Recirculating Pump | 1 | Lower Ground HWL Room | HWL | DDC-LG-PLANT | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
SB-1 | Steam Boiler | 1 | Lower Ground Boiler Room | VENT | DDC-LG-PLANT | Equipment Supplier | 8 | 8 | 1 | 17 | Fire-tube steam boiler with multi-stage burner, fuel-oil fired (typical for hotel laundry) | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies steam pressure, feedwater T, fluegas T+O2 sensors. Boiler equipment provides aux contacts for status/HOA/trip points.
SB-2 | Steam Boiler | 1 | Lower Ground Boiler Room | VENT | DDC-LG-PLANT | Equipment Supplier | 8 | 8 | 1 | 17 | Fire-tube steam boiler with multi-stage burner, fuel-oil fired (typical for hotel laundry) | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies steam pressure, feedwater T, fluegas T+O2 sensors. Boiler equipment provides aux contacts for status/HOA/trip points.
SCHWP-1 | Secondary CHW Pump | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | Equipment Supplier | 4 | 2 | 1 | 7 | (class default not defined — add to equipment-class-defaults.yaml) | TBD | TBD
SCHWP-2 | Secondary CHW Pump | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | Equipment Supplier | 4 | 2 | 1 | 7 | (class default not defined — add to equipment-class-defaults.yaml) | TBD | TBD
SCHWP-3 | Secondary CHW Pump | 1 | 2nd Level Chiller Room | AC | DDC-2F-CHILLER | Equipment Supplier | 4 | 2 | 1 | 7 | (class default not defined — add to equipment-class-defaults.yaml) | TBD | TBD
TEF-1.1 | Exhaust Fan (Toilet) | 1 | GF Main Lobby Toilet | VENT | DDC-GF-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-1.2 | Exhaust Fan (Toilet) | 1 | GF Main Lobby Toilet | VENT | DDC-GF-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-1.3 | Exhaust Fan (Toilet) | 1 | GF Main Lobby Toilet | VENT | DDC-GF-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-1.4 | Exhaust Fan (Toilet) | 1 | GF Main Lobby Toilet | VENT | DDC-GF-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2.1 | Exhaust Fan (Toilet) | 1 | 2nd Floor Toilet | VENT | DDC-2F-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2.2 | Exhaust Fan (Toilet) | 1 | 2nd Floor Toilet | VENT | DDC-2F-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2B.3 | Exhaust Fan (Toilet) | 1 | 2nd Floor BOH Toilet | VENT | DDC-2F-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-30.20 | Exhaust Fan (Toilet) | 1 | 3rd Floor Toilet | VENT | DDC-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3A.1 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity Toilet | VENT | DDC-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3A.2 | Exhaust Fan (Toilet) | 1 | 3rd Floor Amenity Toilet | VENT | DDC-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3B | Exhaust Fan (Toilet) | 1 | 3rd Floor Toilet | VENT | DDC-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3C.1 | Exhaust Fan (Toilet) | 1 | 3rd Floor Toilet | VENT | DDC-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3C.2 | Exhaust Fan (Toilet) | 1 | 3rd Floor Toilet | VENT | DDC-3F | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.1 | Exhaust Fan (Toilet) | 1 | Basement Toilet | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.2 | Exhaust Fan (Toilet) | 1 | Basement Toilet | VENT | DDC-B1-BOH | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.