## Summary
A3 — Cable Schedule Summary
Total field cable runs | 205
Total field cable length (m) | 4293
Total trunk cable length (m) | 800
Total power feed length (m) | 80
GRAND TOTAL cable length (m) | 5173
By cable type (m)
4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 2097
4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 802
Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 796
4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 598

## Field Cables
ID | From | To | Equipment Class | System | Location | Cable Type | Conductors Required | Conductors Specified | Length (m) | I/O Points Carried | Notes
C0001 | DDC-GF-BOH | AHU-1.1 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | Ground Floor BOH | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_gf)
C0002 | DDC-GF-BOH | AHU-1.1 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | Ground Floor BOH | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 25 | 4 | 4 I/O points carried, 4C cable; length 25 m (typical_range:boh_gf)
C0003 | DDC-GF-BOH | AHU-1.1 (ME Contractor) | AHU (Chilled-Water-Served) | AC | Ground Floor BOH | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_gf)
C0004 | DDC-GF-BOH | AHU-1.2 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | Ground Floor BOH | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_gf)
C0005 | DDC-GF-BOH | AHU-1.2 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | Ground Floor BOH | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 25 | 4 | 4 I/O points carried, 4C cable; length 25 m (typical_range:boh_gf)
C0006 | DDC-GF-BOH | AHU-1.2 (ME Contractor) | AHU (Chilled-Water-Served) | AC | Ground Floor BOH | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_gf)
C0007 | DDC-GF-BOH | AHU-1.3 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | Ground Floor BOH | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_gf)
C0008 | DDC-GF-BOH | AHU-1.3 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | Ground Floor BOH | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 25 | 4 | 4 I/O points carried, 4C cable; length 25 m (typical_range:boh_gf)
C0009 | DDC-GF-BOH | AHU-1.3 (ME Contractor) | AHU (Chilled-Water-Served) | AC | Ground Floor BOH | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_gf)
C0010 | DDC-2M-CASINO | AHU-2M.1 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Mezzanine (Casino) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 18 | 5 | 5 I/O points carried, 6C cable; length 18 m (typical_range:casino_2m_localized)
C0011 | DDC-2M-CASINO | AHU-2M.1 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Mezzanine (Casino) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 18 | 4 | 4 I/O points carried, 4C cable; length 18 m (typical_range:casino_2m_localized)
C0012 | DDC-2M-CASINO | AHU-2M.1 (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Mezzanine (Casino) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 18 | 3 | 3 I/O points carried, 4C cable; length 18 m (typical_range:casino_2m_localized)
C0013 | DDC-2M-CASINO | AHU-2M.2 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Mezzanine (Casino) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 18 | 5 | 5 I/O points carried, 6C cable; length 18 m (typical_range:casino_2m_localized)
C0014 | DDC-2M-CASINO | AHU-2M.2 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Mezzanine (Casino) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 18 | 4 | 4 I/O points carried, 4C cable; length 18 m (typical_range:casino_2m_localized)
C0015 | DDC-2M-CASINO | AHU-2M.2 (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Mezzanine (Casino) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 18 | 3 | 3 I/O points carried, 4C cable; length 18 m (typical_range:casino_2m_localized)
C0016 | DDC-2F-BOH | AHU-B.1 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level BOH | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_2f)
C0017 | DDC-2F-BOH | AHU-B.1 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Level BOH | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 25 | 4 | 4 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0018 | DDC-2F-BOH | AHU-B.1 (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level BOH | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0019 | DDC-2F-BOH | AHU-B.2 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level BOH | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_2f)
C0020 | DDC-2F-BOH | AHU-B.2 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Level BOH | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 25 | 4 | 4 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0021 | DDC-2F-BOH | AHU-B.2 (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level BOH | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0022 | DDC-2F-BOH | AHU-B.3 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level BOH | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_2f)
C0023 | DDC-2F-BOH | AHU-B.3 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Level BOH | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 25 | 4 | 4 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0024 | DDC-2F-BOH | AHU-B.3 (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level BOH | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0025 | DDC-2F-BOH | AHU-EL (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level Executive Lounge | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_2f)
C0026 | DDC-2F-BOH | AHU-EL (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Level Executive Lounge | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 25 | 4 | 4 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0027 | DDC-2F-BOH | AHU-EL (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level Executive Lounge | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0028 | DDC-2F-BOH | AHU-FR2 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level Function Room 2 | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_2f)
C0029 | DDC-2F-BOH | AHU-FR2 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Level Function Room 2 | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 25 | 4 | 4 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0030 | DDC-2F-BOH | AHU-FR2 (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level Function Room 2 | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0031 | DDC-2F-BOH | AHU-FR3 (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level Function Room 3 | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_2f)
C0032 | DDC-2F-BOH | AHU-FR3 (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Level Function Room 3 | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 25 | 4 | 4 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0033 | DDC-2F-BOH | AHU-FR3 (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level Function Room 3 | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0034 | DDC-2F-BOH | AHU-PF (BMS Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level Pre-Function | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_2f)
C0035 | DDC-2F-BOH | AHU-PF (Equipment Supplier) | AHU (Chilled-Water-Served) | AC | 2nd Level Pre-Function | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 25 | 4 | 4 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0036 | DDC-2F-BOH | AHU-PF (ME Contractor) | AHU (Chilled-Water-Served) | AC | 2nd Level Pre-Function | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0037 | DDC-2M-CASINO | AIR-ION-2M.1 (BMS Contractor) | Air Ionizer (Casino) | AC | 2nd Mezzanine (Casino) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 1 | 4 | 18 | 1 | 1 I/O points carried, 4C cable; length 18 m (typical_range:casino_2m_localized)
C0038 | DDC-2M-CASINO | AIR-ION-2M.1 (Equipment Supplier) | Air Ionizer (Casino) | AC | 2nd Mezzanine (Casino) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 2 | 4 | 18 | 2 | 2 I/O points carried, 4C cable; length 18 m (typical_range:casino_2m_localized)
C0039 | DDC-2M-CASINO | AIR-ION-2M.2 (BMS Contractor) | Air Ionizer (Casino) | AC | 2nd Mezzanine (Casino) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 1 | 4 | 18 | 1 | 1 I/O points carried, 4C cable; length 18 m (typical_range:casino_2m_localized)
C0040 | DDC-2M-CASINO | AIR-ION-2M.2 (Equipment Supplier) | Air Ionizer (Casino) | AC | 2nd Mezzanine (Casino) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 2 | 4 | 18 | 2 | 2 I/O points carried, 4C cable; length 18 m (typical_range:casino_2m_localized)
C0041 | DDC-2F-CHILLER | CH-1 (BMS Contractor) | Chiller (Package Water-Cooled) | AC | 2nd Level Chiller Room | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 9 | 12 | 12 | 7 | 7 I/O points carried, 12C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0042 | DDC-2F-CHILLER | CH-1 (ME Contractor) | Chiller (Package Water-Cooled) | AC | 2nd Level Chiller Room | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0043 | DDC-2F-CHILLER | CH-2 (BMS Contractor) | Chiller (Package Water-Cooled) | AC | 2nd Level Chiller Room | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 9 | 12 | 12 | 7 | 7 I/O points carried, 12C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0044 | DDC-2F-CHILLER | CH-2 (ME Contractor) | Chiller (Package Water-Cooled) | AC | 2nd Level Chiller Room | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0045 | DDC-2F-CHILLER | CH-3 (BMS Contractor) | Chiller (Package Water-Cooled) | AC | 2nd Level Chiller Room | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 9 | 12 | 12 | 7 | 7 I/O points carried, 12C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0046 | DDC-2F-CHILLER | CH-3 (ME Contractor) | Chiller (Package Water-Cooled) | AC | 2nd Level Chiller Room | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0047 | DDC-2F-CHILLER | CHW-DIFF (BMS Contractor) | CHW Bypass Header | AC | 2nd Level Chiller Room | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0048 | DDC-2F-CHILLER | CHW-RET-HDR (BMS Contractor) | CHW Return Main Header | AC | 2nd Level Chiller Room | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0049 | DDC-2F-CHILLER | CHW-SUP-HDR (BMS Contractor) | CHW Supply Main Header | AC | 2nd Level Chiller Room | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0050 | DDC-2F-CHILLER | COWP-1 (Equipment Supplier) | Condenser Water Pump | AC | 2nd Level Chiller Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0051 | DDC-2F-CHILLER | COWP-2 (Equipment Supplier) | Condenser Water Pump | AC | 2nd Level Chiller Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0052 | DDC-2F-CHILLER | COWP-3 (Equipment Supplier) | Condenser Water Pump | AC | 2nd Level Chiller Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0053 | DDC-RD-PLANT | CT-1 (BMS Contractor) | Cooling Tower | AC | Roof Deck | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 15 | 4 | 4 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0054 | DDC-RD-PLANT | CT-1 (Equipment Supplier) | Cooling Tower | AC | Roof Deck | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0055 | DDC-RD-PLANT | CT-1 (ME Contractor) | Cooling Tower | AC | Roof Deck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0056 | DDC-RD-PLANT | CT-2 (BMS Contractor) | Cooling Tower | AC | Roof Deck | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 15 | 4 | 4 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0057 | DDC-RD-PLANT | CT-2 (Equipment Supplier) | Cooling Tower | AC | Roof Deck | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0058 | DDC-RD-PLANT | CT-2 (ME Contractor) | Cooling Tower | AC | Roof Deck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0059 | DDC-RD-PLANT | CT-3 (BMS Contractor) | Cooling Tower | AC | Roof Deck | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 15 | 4 | 4 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0060 | DDC-RD-PLANT | CT-3 (Equipment Supplier) | Cooling Tower | AC | Roof Deck | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0061 | DDC-RD-PLANT | CT-3 (ME Contractor) | Cooling Tower | AC | Roof Deck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0062 | DDC-RD-PLANT | CT-COMMON (BMS Contractor) | Cooling Tower (Common) | AC | Roof Deck | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 5 | 6 | 15 | 4 | 4 I/O points carried, 6C cable; length 15 m (typical_range:plant_room_rd_plant)
C0063 | DDC-RD-PLANT | CW-HDR (BMS Contractor) | Condenser Water Header | AC | Roof Deck CT Area | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 2 | 4 | 15 | 2 | 2 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0064 | DDC-2M-CASINO | DOAS-2M (BMS Contractor) | DOAS Unit (Casino — with CO/VOC) | VENT | 2nd Mezzanine (Casino) | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 6 | 6 | 18 | 5 | 5 I/O points carried, 6C cable; length 18 m (typical_range:casino_2m_localized)
C0065 | DDC-2M-CASINO | DOAS-2M (Equipment Supplier) | DOAS Unit (Casino — with CO/VOC) | VENT | 2nd Mezzanine (Casino) | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 10 | 12 | 18 | 9 | 9 I/O points carried, 12C cable; length 18 m (typical_range:casino_2m_localized)
C0066 | DDC-2M-CASINO | DOAS-2M (ME Contractor) | DOAS Unit (Casino — with CO/VOC) | VENT | 2nd Mezzanine (Casino) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 18 | 3 | 3 I/O points carried, 4C cable; length 18 m (typical_range:casino_2m_localized)
C0067 | DDC-RD-PLANT | DOAS-RD.1 (BMS Contractor) | DOAS Unit | VENT | Roof Deck | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 8 | 8 | 15 | 6 | 6 I/O points carried, 8C cable; length 15 m (typical_range:plant_room_rd_plant)
C0068 | DDC-RD-PLANT | DOAS-RD.1 (Equipment Supplier) | DOAS Unit | VENT | Roof Deck | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 11 | 12 | 15 | 10 | 10 I/O points carried, 12C cable; length 15 m (typical_range:plant_room_rd_plant)
C0069 | DDC-RD-PLANT | DOAS-RD.1 (ME Contractor) | DOAS Unit | VENT | Roof Deck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 15 | 4 | 4 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0070 | DDC-RD-PLANT | DOAS-RD.2 (BMS Contractor) | DOAS Unit | VENT | Roof Deck | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 8 | 8 | 15 | 6 | 6 I/O points carried, 8C cable; length 15 m (typical_range:plant_room_rd_plant)
C0071 | DDC-RD-PLANT | DOAS-RD.2 (Equipment Supplier) | DOAS Unit | VENT | Roof Deck | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 11 | 12 | 15 | 10 | 10 I/O points carried, 12C cable; length 15 m (typical_range:plant_room_rd_plant)
C0072 | DDC-RD-PLANT | DOAS-RD.2 (ME Contractor) | DOAS Unit | VENT | Roof Deck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 15 | 4 | 4 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0073 | DDC-RD-PLANT | EF-1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Roof Deck | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0074 | DDC-2F-BOH | EF-2.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0075 | DDC-2F-BOH | EF-2.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0076 | DDC-2F-BOH | EF-2.3 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0077 | DDC-2F-BOH | EF-2.4 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0078 | DDC-2F-BOH | EF-2B.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor BOH | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0079 | DDC-2F-BOH | EF-2B.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor BOH | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0080 | DDC-3F | EF-3.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | 3rd Floor | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:amenity_3f)
C0081 | DDC-3F | EF-3.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | 3rd Floor | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:amenity_3f)
C0082 | DDC-3F | EF-3.3 (Equipment Supplier) | Exhaust Fan (General) | VENT | 3rd Floor | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:amenity_3f)
C0083 | DDC-3F | EF-3.4 (Equipment Supplier) | Exhaust Fan (General) | VENT | 3rd Floor | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:amenity_3f)
C0084 | DDC-3F | EF-3B-G (Equipment Supplier) | Exhaust Fan (General) | VENT | 3rd Floor BOH | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:amenity_3f)
C0085 | DDC-3F | EF-3C.1-G (Equipment Supplier) | Exhaust Fan (General) | VENT | 3rd Floor | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:amenity_3f)
C0086 | DDC-B1-BOH | EF-B.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0087 | DDC-B1-BOH | EF-B.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0088 | DDC-B1-BOH | EF-BR.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement Battery Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0089 | DDC-B1-BOH | EF-BR.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement Battery Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0090 | DDC-B1-BOH | EF-BS.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement Service | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0091 | DDC-B1-BOH | EF-BS.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement Service | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0092 | DDC-B1-BOH | EF-FOST.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement FOST Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0093 | DDC-B1-BOH | EF-GL.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement Garbage Lobby | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0094 | DDC-B1-BOH | EF-GL.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement Garbage Lobby | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0095 | DDC-2F-BOH | EF-GS.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor General Service | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0096 | DDC-2F-BOH | EF-GS.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor General Service | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0097 | DDC-B1-BOH | EF-MFR.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement Main Fire Riser | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0098 | DDC-B1-BOH | EF-MP.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement Mech / Pump | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0099 | DDC-2F-BOH | EF-OHRv2 (Equipment Supplier) | Exhaust Fan (General) | VENT | 2nd Floor OHR | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0100 | DDC-B1-BOH | EF-PR.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement Pump Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0101 | DDC-B1-BOH | EF-PR.3 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement Pump Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0102 | DDC-RD-PLANT | EF-RD.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Roof Deck | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0103 | DDC-RD-PLANT | EF-RO.2 (Equipment Supplier) | Exhaust Fan (General) | VENT | Roof Deck | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0104 | DDC-B1-BOH | EF-WS.1 (Equipment Supplier) | Exhaust Fan (General) | VENT | Basement Wash Service | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0105 | DDC-RD-PLANT | HP-HZ (Equipment Supplier) | Heat Pump | HWL | Roof Deck HWL Area | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0106 | DDC-LG-PLANT | HP-LZ (Equipment Supplier) | Heat Pump | HWL | Lower Ground HWL Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0107 | DDC-RD-PLANT | HWH-HZ (BMS Contractor) | Hot Water Header Set | HWL | Roof Deck HWL Area | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0108 | DDC-LG-PLANT | HWH-LZ (BMS Contractor) | Hot Water Header Set | HWL | Lower Ground HWL Room | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0109 | DDC-RD-PLANT | HWT-HZ (BMS Contractor) | Calorifier (Hot Water Storage Tank) | HWL | Roof Deck HWL Area | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 1 | 4 | 15 | 1 | 1 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0110 | DDC-LG-PLANT | HWT-LZ (BMS Contractor) | Calorifier (Hot Water Storage Tank) | HWL | Lower Ground HWL Room | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0111 | DDC-B1-BOH | PAHU-0.1 (BMS Contractor) | Precooled Air Handling Unit | VENT | Basement | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0112 | DDC-B1-BOH | PAHU-0.1 (Equipment Supplier) | Precooled Air Handling Unit | VENT | Basement | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 5 | 6 | 28 | 5 | 5 I/O points carried, 6C cable; length 28 m (typical_range:boh_b1)
C0113 | DDC-B1-BOH | PAHU-0.1 (ME Contractor) | Precooled Air Handling Unit | VENT | Basement | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 28 | 1 | 1 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0114 | DDC-2F-BOH | PAHU-B.1 (BMS Contractor) | Precooled Air Handling Unit | VENT | 2nd Level BOH | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0115 | DDC-2F-BOH | PAHU-B.1 (Equipment Supplier) | Precooled Air Handling Unit | VENT | 2nd Level BOH | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 5 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_2f)
C0116 | DDC-2F-BOH | PAHU-B.1 (ME Contractor) | Precooled Air Handling Unit | VENT | 2nd Level BOH | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 25 | 1 | 1 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0117 | DDC-2F-BOH | PAHU-B.2 (BMS Contractor) | Precooled Air Handling Unit | VENT | 2nd Level BOH | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0118 | DDC-2F-BOH | PAHU-B.2 (Equipment Supplier) | Precooled Air Handling Unit | VENT | 2nd Level BOH | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 5 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_2f)
C0119 | DDC-2F-BOH | PAHU-B.2 (ME Contractor) | Precooled Air Handling Unit | VENT | 2nd Level BOH | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 25 | 1 | 1 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0120 | DDC-2F-BOH | PAHU-B.3 (BMS Contractor) | Precooled Air Handling Unit | VENT | 2nd Level BOH | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0121 | DDC-2F-BOH | PAHU-B.3 (Equipment Supplier) | Precooled Air Handling Unit | VENT | 2nd Level BOH | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 5 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_2f)
C0122 | DDC-2F-BOH | PAHU-B.3 (ME Contractor) | Precooled Air Handling Unit | VENT | 2nd Level BOH | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 25 | 1 | 1 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0123 | DDC-2F-BOH | PAHU-FR (BMS Contractor) | Precooled Air Handling Unit | VENT | 2nd Level Function Rooms | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0124 | DDC-2F-BOH | PAHU-FR (Equipment Supplier) | Precooled Air Handling Unit | VENT | 2nd Level Function Rooms | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 5 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_2f)
C0125 | DDC-2F-BOH | PAHU-FR (ME Contractor) | Precooled Air Handling Unit | VENT | 2nd Level Function Rooms | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 25 | 1 | 1 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0126 | DDC-2F-BOH | PAHU-PF (BMS Contractor) | Precooled Air Handling Unit | VENT | 2nd Level Pre-Function | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0127 | DDC-2F-BOH | PAHU-PF (Equipment Supplier) | Precooled Air Handling Unit | VENT | 2nd Level Pre-Function | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 5 | 6 | 25 | 5 | 5 I/O points carried, 6C cable; length 25 m (typical_range:boh_2f)
C0128 | DDC-2F-BOH | PAHU-PF (ME Contractor) | Precooled Air Handling Unit | VENT | 2nd Level Pre-Function | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 25 | 1 | 1 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0129 | DDC-RD-PLANT | PAHU-r.1 (BMS Contractor) | Precooled Air Handling Unit | VENT | Roof Deck | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0130 | DDC-RD-PLANT | PAHU-r.1 (Equipment Supplier) | Precooled Air Handling Unit | VENT | Roof Deck | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 5 | 6 | 15 | 5 | 5 I/O points carried, 6C cable; length 15 m (typical_range:plant_room_rd_plant)
C0131 | DDC-RD-PLANT | PAHU-r.1 (ME Contractor) | Precooled Air Handling Unit | VENT | Roof Deck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 15 | 1 | 1 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0132 | DDC-RD-PLANT | PAHU-r.2 (BMS Contractor) | Precooled Air Handling Unit | VENT | Roof Deck | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 4 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0133 | DDC-RD-PLANT | PAHU-r.2 (Equipment Supplier) | Precooled Air Handling Unit | VENT | Roof Deck | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 5 | 6 | 15 | 5 | 5 I/O points carried, 6C cable; length 15 m (typical_range:plant_room_rd_plant)
C0134 | DDC-RD-PLANT | PAHU-r.2 (ME Contractor) | Precooled Air Handling Unit | VENT | Roof Deck | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 1 | 4 | 15 | 1 | 1 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0135 | DDC-2F-CHILLER | PCHWP-1 (BMS Contractor) | Primary CHW Pump | AC | 2nd Level Chiller Room | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0136 | DDC-2F-CHILLER | PCHWP-1 (Equipment Supplier) | Primary CHW Pump | AC | 2nd Level Chiller Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0137 | DDC-2F-CHILLER | PCHWP-2 (BMS Contractor) | Primary CHW Pump | AC | 2nd Level Chiller Room | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 1 | 4 | 12 | 1 | 1 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0138 | DDC-2F-CHILLER | PCHWP-2 (Equipment Supplier) | Primary CHW Pump | AC | 2nd Level Chiller Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0139 | DDC-2F-CHILLER | PCHWP-3 (Equipment Supplier) | Primary CHW Pump (Standby) | AC | 2nd Level Chiller Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0140 | DDC-RD-PLANT | RP-HZ (Equipment Supplier) | Recirculating Pump | HWL | Roof Deck HWL Area | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 15 | 3 | 3 I/O points carried, 4C cable; length 15 m (typical_range:plant_room_rd_plant)
C0141 | DDC-LG-PLANT | RP-LZ (Equipment Supplier) | Recirculating Pump | HWL | Lower Ground HWL Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 12 | 3 | 3 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0142 | DDC-LG-PLANT | SB-1 (BMS Contractor) | Steam Boiler | VENT | Lower Ground Boiler Room | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 7 | 8 | 12 | 6 | 6 I/O points carried, 8C cable; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0143 | DDC-LG-PLANT | SB-1 (Equipment Supplier) | Steam Boiler | VENT | Lower Ground Boiler Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0144 | DDC-LG-PLANT | SB-2 (BMS Contractor) | Steam Boiler | VENT | Lower Ground Boiler Room | 4C × 1.5 mm² shielded FRLS (BMS signal — BMS-supplied sensors) | 7 | 8 | 12 | 6 | 6 I/O points carried, 8C cable; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0145 | DDC-LG-PLANT | SB-2 (Equipment Supplier) | Steam Boiler | VENT | Lower Ground Boiler Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 2 | 4 | 12 | 2 | 2 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0146 | DDC-2F-CHILLER | SCHWP-1 (Equipment Supplier) | Secondary CHW Pump | AC | 2nd Level Chiller Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0147 | DDC-2F-CHILLER | SCHWP-2 (Equipment Supplier) | Secondary CHW Pump | AC | 2nd Level Chiller Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0148 | DDC-2F-CHILLER | SCHWP-3 (Equipment Supplier) | Secondary CHW Pump | AC | 2nd Level Chiller Room | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 4 | 4 | 12 | 4 | 4 I/O points carried, 4C cable; length 12 m (typical_range:plant_room_chiller_2f)
C0149 | DDC-GF-BOH | TEF-1.1 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | GF Main Lobby Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_gf)
C0150 | DDC-GF-BOH | TEF-1.2 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | GF Main Lobby Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_gf)
C0151 | DDC-GF-BOH | TEF-1.3 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | GF Main Lobby Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_gf)
C0152 | DDC-GF-BOH | TEF-1.4 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | GF Main Lobby Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_gf)
C0153 | DDC-2F-BOH | TEF-2.1 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 2nd Floor Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0154 | DDC-2F-BOH | TEF-2.2 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 2nd Floor Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0155 | DDC-2F-BOH | TEF-2B.3 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 2nd Floor BOH Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 25 | 3 | 3 I/O points carried, 4C cable; length 25 m (typical_range:boh_2f)
C0156 | DDC-3F | TEF-30.20 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:amenity_3f)
C0157 | DDC-3F | TEF-3A.1 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor Amenity Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:amenity_3f)
C0158 | DDC-3F | TEF-3A.2 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor Amenity Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:amenity_3f)
C0159 | DDC-3F | TEF-3B (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:amenity_3f)
C0160 | DDC-3F | TEF-3C.1 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:amenity_3f)
C0161 | DDC-3F | TEF-3C.2 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | 3rd Floor Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 35 | 3 | 3 I/O points carried, 4C cable; length 35 m (typical_range:amenity_3f)
C0162 | DDC-B1-BOH | TEF-B.1 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | Basement Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0163 | DDC-B1-BOH | TEF-B.2 (Equipment Supplier) | Exhaust Fan (Toilet) | VENT | Basement Toilet | 4C × 1.5 mm² FRLS (equipment auxiliary contacts — status/HOA/trip/start-stop) | 3 | 4 | 28 | 3 | 3 I/O points carried, 4C cable; length 28 m (typical_range:boh_b1)
C0164 | DDC-2F-CHILLER | CH-1 (Network) | Chiller (Package Water-Cooled) | AC | 2nd Level Chiller Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_chiller_2f)
C0165 | DDC-2F-CHILLER | CH-2 (Network) | Chiller (Package Water-Cooled) | AC | 2nd Level Chiller Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_chiller_2f)
C0166 | DDC-2F-CHILLER | CH-3 (Network) | Chiller (Package Water-Cooled) | AC | 2nd Level Chiller Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_chiller_2f)
C0167 | DDC-2F-CHILLER | PCHWP-1 (Network) | Primary CHW Pump | AC | 2nd Level Chiller Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_chiller_2f)
C0168 | DDC-2F-CHILLER | PCHWP-2 (Network) | Primary CHW Pump | AC | 2nd Level Chiller Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_chiller_2f)
C0169 | DDC-2F-CHILLER | SCHWP-1 (Network) | Secondary CHW Pump | AC | 2nd Level Chiller Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_chiller_2f)
C0170 | DDC-2F-CHILLER | SCHWP-2 (Network) | Secondary CHW Pump | AC | 2nd Level Chiller Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_chiller_2f)
C0171 | DDC-2F-CHILLER | SCHWP-3 (Network) | Secondary CHW Pump | AC | 2nd Level Chiller Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_chiller_2f)
C0172 | DDC-LG-PLANT | SB-1 (Network) | Steam Boiler | VENT | Lower Ground Boiler Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0173 | DDC-LG-PLANT | SB-2 (Network) | Steam Boiler | VENT | Lower Ground Boiler Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0174 | DDC-RD-PLANT | DOAS-RD.1 (Network) | DOAS Unit | VENT | Roof Deck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:plant_room_rd_plant)
C0175 | DDC-RD-PLANT | DOAS-RD.2 (Network) | DOAS Unit | VENT | Roof Deck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:plant_room_rd_plant)
C0176 | DDC-RD-PLANT | PAHU-r.1 (Network) | Precooled Air Handling Unit | VENT | Roof Deck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:plant_room_rd_plant)
C0177 | DDC-RD-PLANT | PAHU-r.2 (Network) | Precooled Air Handling Unit | VENT | Roof Deck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 15 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 15 m (typical_range:plant_room_rd_plant)
C0178 | DDC-2M-CASINO | DOAS-2M (Network) | DOAS Unit (Casino — with CO/VOC) | VENT | 2nd Mezzanine (Casino) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 18 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 18 m (typical_range:casino_2m_localized)
C0179 | DDC-2M-CASINO | AHU-2M.1 (Network) | AHU (Chilled-Water-Served) | AC | 2nd Mezzanine (Casino) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 18 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 18 m (typical_range:casino_2m_localized)
C0180 | DDC-2M-CASINO | AHU-2M.2 (Network) | AHU (Chilled-Water-Served) | AC | 2nd Mezzanine (Casino) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 18 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 18 m (typical_range:casino_2m_localized)
C0181 | DDC-2M-CASINO | AIR-ION-2M.1 (Network) | Air Ionizer (Casino) | AC | 2nd Mezzanine (Casino) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 18 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 18 m (typical_range:casino_2m_localized)
C0182 | DDC-2M-CASINO | AIR-ION-2M.2 (Network) | Air Ionizer (Casino) | AC | 2nd Mezzanine (Casino) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 18 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 18 m (typical_range:casino_2m_localized)
C0183 | DDC-2F-BOH | AHU-B.1 (Network) | AHU (Chilled-Water-Served) | AC | 2nd Level BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0184 | DDC-2F-BOH | AHU-B.2 (Network) | AHU (Chilled-Water-Served) | AC | 2nd Level BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0185 | DDC-2F-BOH | AHU-B.3 (Network) | AHU (Chilled-Water-Served) | AC | 2nd Level BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0186 | DDC-2F-BOH | AHU-PF (Network) | AHU (Chilled-Water-Served) | AC | 2nd Level Pre-Function | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0187 | DDC-2F-BOH | AHU-EL (Network) | AHU (Chilled-Water-Served) | AC | 2nd Level Executive Lounge | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0188 | DDC-2F-BOH | AHU-FR2 (Network) | AHU (Chilled-Water-Served) | AC | 2nd Level Function Room 2 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0189 | DDC-2F-BOH | AHU-FR3 (Network) | AHU (Chilled-Water-Served) | AC | 2nd Level Function Room 3 | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0190 | DDC-2F-BOH | PAHU-B.1 (Network) | Precooled Air Handling Unit | VENT | 2nd Level BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0191 | DDC-2F-BOH | PAHU-B.2 (Network) | Precooled Air Handling Unit | VENT | 2nd Level BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0192 | DDC-2F-BOH | PAHU-B.3 (Network) | Precooled Air Handling Unit | VENT | 2nd Level BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0193 | DDC-2F-BOH | PAHU-PF (Network) | Precooled Air Handling Unit | VENT | 2nd Level Pre-Function | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0194 | DDC-2F-BOH | PAHU-FR (Network) | Precooled Air Handling Unit | VENT | 2nd Level Function Rooms | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0195 | DDC-GF-BOH | AHU-1.1 (Network) | AHU (Chilled-Water-Served) | AC | Ground Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_gf)
C0196 | DDC-GF-BOH | AHU-1.2 (Network) | AHU (Chilled-Water-Served) | AC | Ground Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_gf)
C0197 | DDC-GF-BOH | AHU-1.3 (Network) | AHU (Chilled-Water-Served) | AC | Ground Floor BOH | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_gf)
C0198 | DDC-B1-BOH | PAHU-0.1 (Network) | Precooled Air Handling Unit | VENT | Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 28 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 28 m (typical_range:boh_b1)
C0199 | DDC-LG-PLANT | MPM-MAIN (Network) | Multifunction Power Meter (Main) | EL | Lower Ground Main Switchroom | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0200 | DDC-2F-CHILLER | MPM-CHILLER (Network) | Multifunction Power Meter (Feeder) | EL | 2nd Level Chiller MCC | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_chiller_2f)
C0201 | DDC-2F-BOH | MPM-AHU-2F (Network) | Multifunction Power Meter (Feeder) | EL | 2nd Level AHU MCC | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_2f)
C0202 | DDC-GF-BOH | MPM-AHU-GF (Network) | Multifunction Power Meter (Feeder) | EL | Ground Floor AHU MCC | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_gf)
C0203 | DDC-LG-PLANT | MPM-LIGHT-A (Network) | Multifunction Power Meter (Feeder) | EL | Lower Ground Lighting Panel A | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0204 | DDC-LG-PLANT | MPM-LIGHT-B (Network) | Multifunction Power Meter (Feeder) | EL | Lower Ground Lighting Panel B | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 12 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 12 m (typical_range:plant_room_lg_boiler_hwl)
C0205 | DDC-GF-BOH | FACP-GW (Network) | FACP Gateway | FDAS | Ground Floor Fire Command Center | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 25 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 25 m (typical_range:boh_gf)

## Trunks
ID | From | To | Cable Type | Length (m) | Notes
T0206 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for 2nd Floor — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0207 | BMS Server Room (head-end) | All BMS panels at 3rd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for 3rd Floor — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0208 | BMS Server Room (head-end) | All BMS panels at Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Basement — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0209 | BMS Server Room (head-end) | All BMS panels at Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Ground — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0210 | BMS Server Room (head-end) | All BMS panels at Lower Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Lower Ground — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0211 | BMS Server Room (head-end) | BMS panel controllers (per topology id mstp_field_backbone) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 250 | MS/TP field backbone connects DDC-2F-CHILLER, DDC-2F-BOH, DDC-2M-CASINO, DDC-RD-PLANT, DDC-LG-PLANT, DDC-GF-BOH, DDC-B1-BOH, DDC-3F. Routed via service-core IDF stack on west end (per ECE auxiliary layouts) + horizontal BOH-corridor tray on each panel's floor. Vertical span B1 → RD ≈ 13 floors × 4.5 m = 58.5 m + 8 panel-side horizontal segments at ~25 m each ≈ 200 m + 25% routing factor ≈ 250 m typical.
T0212 | BMS Server Room (head-end) | BMS panel controllers (per topology id bacnet_ip_backbone) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 150 | BACnet/IP backbone is fibre + Cat6: head-end (Lower Ground IT room per Q-011) → core switch → riser fibre to per-floor IDF edge switches → Cat6 to each DDC field panel. Vertical fibre run LG → RD ≈ 13 floors × 4.5 m = 58.5 m. 8 horizontal fibre segments at ~5 m each. Total ≈ 100-150 m measured; allow 150 m typical.

## Panel Power Feeds
ID | From | To | Cable Type | Length (m) | Notes
P0213 | Local panelboard / EE-supplied feeder | DDC-2F-BOH — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 10 m (typical_range:panel_power_feed_local)
P0214 | Local panelboard / EE-supplied feeder | DDC-2F-CHILLER — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 10 m (typical_range:panel_power_feed_local)
P0215 | Local panelboard / EE-supplied feeder | DDC-2M-CASINO — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 10 m (typical_range:panel_power_feed_local)
P0216 | Local panelboard / EE-supplied feeder | DDC-3F — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 10 m (typical_range:panel_power_feed_local)
P0217 | Local panelboard / EE-supplied feeder | DDC-B1-BOH — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 10 m (typical_range:panel_power_feed_local)
P0218 | Local panelboard / EE-supplied feeder | DDC-GF-BOH — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 10 m (typical_range:panel_power_feed_local)
P0219 | Local panelboard / EE-supplied feeder | DDC-LG-PLANT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 10 m (typical_range:panel_power_feed_local)
P0220 | Local panelboard / EE-supplied feeder | DDC-RD-PLANT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 10 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 10 m (typical_range:panel_power_feed_local)