## Summary
A4 — Panel Schedule Summary
Total panels | 8
Total physical I/O | 561
Total HLI subpoints | 141
Total network drops | 42
Total I/O points | 744
Estimated total controllers | 19
Estimated total power (W) | 685

## Panel Schedule
Panel | Location | System Scope | Equipment Count | Physical I/O | HLI Subpoints | Network Drops | Total I/O | DDC Controllers | Network Gateway | Total Controllers | Power (W) | Enclosure
DDC-2F-BOH | 2nd Floor / 2nd Floor BOH / 2nd Floor BOH Toilet / 2nd Floor General Service / 2nd Floor OHR / 2nd Floor Toilet / 2nd Level AHU MCC / 2nd Level BOH / 2nd Level Executive Lounge / 2nd Level Function Room 2 / 2nd Level Function Room 3 / 2nd Level Function Rooms / 2nd Level Pre-Function | AC, EL, VENT | 25 | 165 | 25 | 13 | 203 | 5 | 1 | 5 | 190 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
DDC-2F-CHILLER | 2nd Level Chiller MCC / 2nd Level Chiller Room | AC, EL | 16 | 72 | 65 | 9 | 146 | 2 | 1 | 2 | 95 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
DDC-2M-CASINO | 2nd Mezzanine (Casino) | AC, VENT | 5 | 47 | 8 | 5 | 60 | 2 | 1 | 2 | 75 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
DDC-3F | 3rd Floor / 3rd Floor Amenity Toilet / 3rd Floor BOH / 3rd Floor Toilet | VENT | 12 | 36 | 0 | 0 | 36 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
DDC-B1-BOH | Basement / Basement Battery Room / Basement FOST Room / Basement Garbage Lobby / Basement Main Fire Riser / Basement Mech / Pump / Basement Pump Room / Basement Service / Basement Toilet / Basement Wash Service | VENT | 17 | 57 | 2 | 1 | 60 | 2 | 1 | 2 | 55 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
DDC-GF-BOH | GF Main Lobby Toilet / Ground Floor AHU MCC / Ground Floor BOH / Ground Floor Fire Command Center | AC, EL, FDAS, VENT | 9 | 48 | 10 | 5 | 63 | 2 | 1 | 2 | 75 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
DDC-LG-PLANT | Lower Ground Boiler Room / Lower Ground HWL Room / Lower Ground Lighting Panel A / Lower Ground Lighting Panel B / Lower Ground Main Switchroom | EL, HWL, VENT | 9 | 26 | 19 | 5 | 50 | 1 | 1 | 2 | 75 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
DDC-RD-PLANT | Roof Deck / Roof Deck CT Area / Roof Deck HWL Area | AC, HWL, VENT | 16 | 110 | 12 | 4 | 126 | 3 | 1 | 3 | 95 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare

## Equipment per Panel
Panel | Equipment Instance
DDC-2F-BOH | AHU-B.1
DDC-2F-BOH | AHU-B.2
DDC-2F-BOH | AHU-B.3
DDC-2F-BOH | AHU-EL
DDC-2F-BOH | AHU-FR2
DDC-2F-BOH | AHU-FR3
DDC-2F-BOH | AHU-PF
DDC-2F-BOH | EF-2.1
DDC-2F-BOH | EF-2.2
DDC-2F-BOH | EF-2.3
DDC-2F-BOH | EF-2.4
DDC-2F-BOH | EF-2B.1
DDC-2F-BOH | EF-2B.2
DDC-2F-BOH | EF-GS.1
DDC-2F-BOH | EF-GS.2
DDC-2F-BOH | EF-OHRv2
DDC-2F-BOH | MPM-AHU-2F
DDC-2F-BOH | PAHU-B.1
DDC-2F-BOH | PAHU-B.2
DDC-2F-BOH | PAHU-B.3
DDC-2F-BOH | PAHU-FR
DDC-2F-BOH | PAHU-PF
DDC-2F-BOH | TEF-2.1
DDC-2F-BOH | TEF-2.2
DDC-2F-BOH | TEF-2B.3
DDC-2F-CHILLER | CH-1
DDC-2F-CHILLER | CH-2
DDC-2F-CHILLER | CH-3
DDC-2F-CHILLER | CHW-DIFF
DDC-2F-CHILLER | CHW-RET-HDR
DDC-2F-CHILLER | CHW-SUP-HDR
DDC-2F-CHILLER | COWP-1
DDC-2F-CHILLER | COWP-2
DDC-2F-CHILLER | COWP-3
DDC-2F-CHILLER | MPM-CHILLER
DDC-2F-CHILLER | PCHWP-1
DDC-2F-CHILLER | PCHWP-2
DDC-2F-CHILLER | PCHWP-3
DDC-2F-CHILLER | SCHWP-1
DDC-2F-CHILLER | SCHWP-2
DDC-2F-CHILLER | SCHWP-3
DDC-2M-CASINO | AHU-2M.1
DDC-2M-CASINO | AHU-2M.2
DDC-2M-CASINO | AIR-ION-2M.1
DDC-2M-CASINO | AIR-ION-2M.2
DDC-2M-CASINO | DOAS-2M
DDC-3F | EF-3.1
DDC-3F | EF-3.2
DDC-3F | EF-3.3
DDC-3F | EF-3.4
DDC-3F | EF-3B-G
DDC-3F | EF-3C.1-G
DDC-3F | TEF-30.20
DDC-3F | TEF-3A.1
DDC-3F | TEF-3A.2
DDC-3F | TEF-3B
DDC-3F | TEF-3C.1
DDC-3F | TEF-3C.2
DDC-B1-BOH | EF-B.1
DDC-B1-BOH | EF-B.2
DDC-B1-BOH | EF-BR.1
DDC-B1-BOH | EF-BR.2
DDC-B1-BOH | EF-BS.1
DDC-B1-BOH | EF-BS.2
DDC-B1-BOH | EF-FOST.1
DDC-B1-BOH | EF-GL.1
DDC-B1-BOH | EF-GL.2
DDC-B1-BOH | EF-MFR.1
DDC-B1-BOH | EF-MP.1
DDC-B1-BOH | EF-PR.1
DDC-B1-BOH | EF-PR.3
DDC-B1-BOH | EF-WS.1
DDC-B1-BOH | PAHU-0.1
DDC-B1-BOH | TEF-B.1
DDC-B1-BOH | TEF-B.2
DDC-GF-BOH | AHU-1.1
DDC-GF-BOH | AHU-1.2
DDC-GF-BOH | AHU-1.3
DDC-GF-BOH | FACP-GW
DDC-GF-BOH | MPM-AHU-GF
DDC-GF-BOH | TEF-1.1
DDC-GF-BOH | TEF-1.2
DDC-GF-BOH | TEF-1.3
DDC-GF-BOH | TEF-1.4
DDC-LG-PLANT | HP-LZ
DDC-LG-PLANT | HWH-LZ
DDC-LG-PLANT | HWT-LZ
DDC-LG-PLANT | MPM-LIGHT-A
DDC-LG-PLANT | MPM-LIGHT-B
DDC-LG-PLANT | MPM-MAIN
DDC-LG-PLANT | RP-LZ
DDC-LG-PLANT | SB-1
DDC-LG-PLANT | SB-2
DDC-RD-PLANT | CT-1
DDC-RD-PLANT | CT-2
DDC-RD-PLANT | CT-3
DDC-RD-PLANT | CT-COMMON
DDC-RD-PLANT | CW-HDR
DDC-RD-PLANT | DOAS-RD.1
DDC-RD-PLANT | DOAS-RD.2
DDC-RD-PLANT | EF-1
DDC-RD-PLANT | EF-RD.1
DDC-RD-PLANT | EF-RO.2
DDC-RD-PLANT | HP-HZ
DDC-RD-PLANT | HWH-HZ
DDC-RD-PLANT | HWT-HZ
DDC-RD-PLANT | PAHU-r.1
DDC-RD-PLANT | PAHU-r.2
DDC-RD-PLANT | RP-HZ