Table of Contents

# Internal Team Notes — 2026-04-kingsford-bms-AB6

Audience: the proposal team running the next pass on this project.

This document compiles actionable items pulled from the project’s working artifacts. Each section is what to do next — verify, refine, or reconsider — to improve the proposal before it goes to the customer or as part of an RFQ-response cycle.

Sources compiled:

- 07-assumptions.md — assumptions to verify or refine

- 08-customer-clarifications.md — questions to send the customer

- 99-decision-log.md — decisions worth revisiting

- 03-doc-inventory.md — gap analysis on customer inputs

- 05-working-docs/A3-cable-schedule.yaml — cable-length fallbacks to verify

- 05-working-docs/D3-risk-register.md — project risks (if present)

- 09-rfq-package/ — RFQ packages (cost-reduction via competitive bidding)

## 1. Customer clarifications (RFI list)

15 open questions to send the customer. Each has a documented default assumption with cost / scope impact. Resolving these is the highest-leverage path to refining the proposal — every answered Q-NNN may flip an open assumption from Assumed to Confirmed and reduce contingency.

| ID | Question | Default assumed | What an answer changes |
| --- | --- | --- | --- |
| Q-001 | The cover letter uses the wording “Rehabilitation” but the EE and BMS Construc… | Stage classification drives demolition scope, after-hours pr | Greenfield (A-001) |
| Q-002 | Required warranty period and conditions? | Drives commercial loading. | 1 year hardware + workmanship warranty (A-002) |
| Q-003 | Post-handover maintenance contract — separate scope or included in this proposal… | Affects commercial loading + helpdesk scope. | Excluded from this proposal; offered as optional addendum (A |
| Q-004 | Megaworld DRC-004-2024 Section 9 — please share the brand-approval list. Interna… | Brand substitutions during shop-drawing review can shift cos | Siemens / Dell (A-003) |
| Q-005 | Architectural floor plans — please share. | Required for accurate cable-route measurement (corridor leng | Cable lengths fall back to typical ranges per `A3-route-leng |
| Q-006 | Mechanical (HVAC) layouts — equipment locations, ductwork routing, FCU/VAV place… | HVAC equipment locations confirm guestroom-zone counts, FCU/ | Equipment counts inferred from points-list zoning + typical |
| Q-007 | If existing BMS is being replaced (per Q-001 outcome): please share existing con… | Drives demolition + reuse decisions. | N/A unless Q-001 answers “rehab” (A-006) |
| Q-008 | Has an “EL” (Electrical) BMS points-list partition been issued or is one forthco… | Defines whether power-quality / energy-monitoring scope is i | Limited to power meters at major load centers per Megaworld |
| Q-009 | Plumbing BMS scope — Part C of the points list covers domestic hot-water only. S… | Defines BMS scope vs. ME-package monitoring. | BMS scope limited to domestic hot-water per Part C (A-008) |
| Q-010 | Building stack — please confirm: Basement / LG / GF / 2F amenity / 3F amenity / … | Drives equipment-instance count for guestroom-zone aggregati | Stack inferred from EE plan + points-list zoning (A-009) |
| Q-011 | BMS Server + control room location — typically in Lower Ground or Ground Floor B… | Drives head-end siting + uplink trunk lengths. | Lower Ground IT/BOH room assumed |
| Q-012 | Casino / gaming-floor adjacency — Kingsford casino floors share the building. Ar… | Adds CO-sensor scope at gaming-floor return air. | Not in scope unless customer confirms |
| Q-013 | Number of typical guestroom FCUs per floor and per FCU-class — verify against M-… | Drives guestroom field-device count. | ~24 FCUs per typical guestroom floor (× 6 typical floors = 1 |
| Q-014 | Power Riser Diagram (sheet EE-24 per cover letter) and Load Schedules (EE-21/22/… | A5 (network architecture) + A7 (power provisions) need the r | Single-shaft riser + standard 1.5mm² copper feeder per panel |
| Q-015 | DDC field-controller protocol confirmation — BMS-03 P&ID sheet shows NETWORK row… | Drives field-bus topology + cable spec. | BACnet MS/TP at field + BACnet/IP at head-end (per DRC-004) |

## 2. Verification action items (against drawings, on site, with vendors)

### Cable lengths — fallback rows to verify

Cables tagged legacy_fallback, typical_range:*, or fallback_a001 use agent-reasoned typical-range estimates rather than direct drawing measurements. These are the audit-XLSX rows the team should prioritize when the next set of drawings lands or when site walkthroughs become possible.

| Method tag | Count | Sample row ID |
| --- | --- | --- |
| typical_range:boh_2f | 61 | C0016 |
| typical_range:plant_room_rd_plant | 34 | C0053 |
| typical_range:plant_room_chiller_2f | 29 | C0041 |
| typical_range:boh_b1 | 20 | C0086 |
| typical_range:boh_gf | 18 | C0001 |
| typical_range:casino_2m_localized | 18 | C0010 |
| typical_range:plant_room_lg_boiler_hwl | 13 | C0106 |
| typical_range:amenity_3f | 12 | C0080 |
| typical_range:panel_power_feed_local | 8 | P0213 |
| unknown | 5 | T0206 |
| typical_range | 2 | T0211 |

Open 13-A3-cable-schedule-AUDIT.xlsx to filter and prioritize.

### Other verification items

- Equipment counts — verify against mechanical floor plans where the agent inferred quantities (see open assumptions where Status: Open and category contains ‘count’).

- Panel locations — confirm against architectural drawings and walk the building if accessible.

- Drawing scale calibrations — if any A-NNN entries record drawing-scale calibration assumptions (e.g., grid-bay calibration), spot-check against a second known dimension before the proposal goes out.

- Vendor specifications — for every Equipment Supplier C/O cable / interface, confirm that the supplier’s panel architecture matches the assumed BMS-side interface (HLI vs. hardwired DI/DO).

## 3. Cost-reduction opportunities

### RFQ packages — competitive bidding

The agent prepared 12 RFQ packages categorized by supplier type. Issuing all of them and comparing 3+ quotes per package is the standard cost-reduction lever. Especially impactful for high-value categories:

- bms-controllers-and-panels — typically 5–15% savings vs. catalog pricing on competitive bid

- field-sensors-hvac — typically 5–15% savings vs. catalog pricing on competitive bid

- head-end-servers-workstations — typically 5–15% savings vs. catalog pricing on competitive bid

- network-active — typically 5–15% savings vs. catalog pricing on competitive bid

- power-meters — typically 5–15% savings vs. catalog pricing on competitive bid

- valves-actuators — typically 5–15% savings vs. catalog pricing on competitive bid

Full list in 09-rfq-package/. Send these as soon as the proposal’s commercial side is firm — supplier turnaround is typically 2–4 weeks.

### Other cost levers

- Cable specifications — confirm with the customer whether the assumed jacket rating (e.g., FRLS) is mandated or whether a less-specified cable is acceptable in non-occupied spaces. Material cost difference can be 10–20% on cabling.

- Spare-conductor strategy — current strategy provides 15–25% spares per I/O class. If the customer is willing to accept lower spare margins (commit to the I/O list as-final), cable size drops and material cost reduces 5–10%.

- Make/model consolidation — RFQ packages currently call for spec-level equivalent items. If the customer accepts a single-vendor list (one controller brand, one valve brand), the team can negotiate volume discounts. Document any such consolidation in a new Q-NNN.

- Owner-furnished items — review C1 contractor/owner matrix; items currently assigned to BMS scope that the owner could supply directly (e.g., off-the-shelf workstations, network switches if customer has IT preferences) reduce BMS material markup.

## 4. Risks and decisions to revisit

### Risk register highlights

Open risks from D3-risk-register.md worth re-evaluating before issue:

- R-01 — Q-001 wording mismatch — customer confirms project IS rehabilitation requiring demolition + cutover

- R-02 — Q-004 brand-approval list disqualifies Siemens / Dell — Megaworld DRC-004 names different tier-1 bra

- R-03 — EE Plan re-extraction (Q-014) reveals different per-circuit IDs than placeholder, requiring panel-po

- R-04 — Q-008 EL points-list addendum issued late, requiring metering-scope variation | Low (none currently

- R-05 — Q-009 plumbing scope expands to include sump / fire / transfer pumps | Low | Low-Medium (~PHP 0.3-0.

- R-06 — Casino fit-out delays Air Ionizer Modbus integration spec, slipping integrated testing | Medium | Me

- R-07 — Architectural / mechanical layouts (Q-005 / Q-006) drop later than expected, forcing late-cycle cabl

- R-08 — Megaworld review cycles slow shop-drawing approval | Low (one cycle observed in Construction Bulleti

- R-09 — Cooling-tower blowdown corrosion sensor calibration (chemistry-dependent) requires post-install adju

- R-10 — Building stack assumption (A-009) wrong on guestroom-floor key count → BMS scope marginally affected

### Recent decisions worth revisiting

Decisions made during proposal generation. Review whether each is still right given any new customer answers or drawings received since the decision was made.

- D-001 — Project classification: Greenfield, not Rehabilitation

- D-002 — Scope shape: Pattern 1 (Turnkey BMS)

- D-003 — Customer KB: STUB (megaworld) — internal preferred brands apply

- D-004 — Drawing extraction: 5 parallel subagents, image-batch capped per Patch B

- D-005 — Equipment-aggregation strategy (PATCH A — committed BEFORE A1 authoring)

- D-006 — AB-Run-6 finding: image-batch dimension limit on individual large pages

- D-007 — Aggregation execution check (post-Phase 5a entry will close)

## 5. Open assumptions to refine

0 assumptions in ‘Open’ status (out of 0 total). Each one is something the proposal currently treats as a known quantity but isn’t actually confirmed. The team should pair each open assumption with the corresponding Q-NNN and chase the customer’s answer.

## 6. Process improvements queued

Items the methodology audit and A/B regression runs flagged for the next playbook pass. These don’t block this proposal but will improve the next one:

- Conduit ratio — currently 30% of total cable length unless overridden. Project-tuned override available via B4-site-factors.yaml (see Op#11).

- Commercial rates — overhead 20% / contingency 7.5% / VAT 12% are defaults. Project-tuned override via 06-commercial-rates.yaml based on risk-register score.

- Cable specs — currently project-blind. Consider authoring A3-cable-spec-rules.yaml per _playbook/sub-routines/build-cable-schedule.md for explicit jurisdiction / brand reasoning.

- MS/TP trunk topology — formula-based fallback; ideally derived from actual A4 panel locations.

## 7. Defensibility check — what’s already strong

Reassurance for the team — items the agent already handled to a defensible standard:

- Every BOQ line traces to a working doc; every working doc cites sources

- Drawing-availability triage committed in writing in 03-doc-inventory.md (per Op#10)

- All assumptions are documented with rationale + impact-if-wrong

- 13-file deliverables package ready for issue with no missing artifacts

- Audit XLSX layer (per Principle F) makes verification work tractable

Generated by _playbook/tools/generate-internal-notes.py. Re-run after any update to the project’s working docs to refresh.