## Summary
A3 — Cable Schedule, Audit View
Project | Kingsford Hotel Bacolod BMS
Canonical source | A3-cable-schedule.yaml
How to record corrections | Edit the canonical YAML directly — add a verification: block to the affected row(s)
Totals
Total cables | 200
Total length (m) | 6,810
Field cables | 175
Trunk cables | 7
Panel power feeds | 18
Verification status
Status | Count | % of total
verified | 0 | 0%
needs_correction | 0 | 0%
uncertain | 0 | 0%
unverified | 200 | 100%
⚠ Known weak points
Cable lengths are estimates based on assumption A-001 (30 m average panel-to-device run, 80 m trunk per floor). Field-verified lengths typically vary by ±20% per cable. THIS IS THE SYSTEM'S WEAKEST AUTO-GENERATED QUANTITY — please verify before issuing the BOQ to the customer.
How corrections flow
1. Open A3-cable-schedule.yaml in any text editor.
2. Find the affected row by ID (column A in the Detail sheet).
3. Add a verification: block — see the 'Verification schema' sheet for the template.
4. Re-run: python3 _playbook/tools/generate-deliverables.py <project>
5. Corrections flow through B4 manhours, BOQ material costs, and final deliverables automatically.

## By Panel
Panel | Cable count | Total length (m)
PNL-VENT-L3 | 27 | 810
PNL-VENT-BSMT | 16 | 480
PNL-VENT-L2 | 13 | 390
PNL-AHU-L2 | 12 | 360
PNL-CHWP-GND | 12 | 360
PNL-CT-RD | 12 | 360
PNL-CHWP-L2 | 11 | 330
PNL-PL-LZ | 10 | 300
PNL-EE-DIST | 10 | 300
PNL-CH-PLANT-GND | 9 | 270
PNL-VENT-GF | 9 | 270
PNL-DOAS-RD | 8 | 240
PNL-PAHU-RD | 8 | 240
PNL-DOAS-L2 | 4 | 120
PNL-PL-HZ | 4 | 120
PNL-BL-LZ | 4 | 120
PNL-VENT-RD | 3 | 90
PNL-EE-MAIN | 3 | 90
TOTAL (field cables) | 175 | 5250

## By Floor
Floor | Cable count | Total length (m)
2nd Floor | 40 | 1200
Roofdeck | 35 | 1050
3rd Floor | 27 | 810
GND | 21 | 630
Basement | 16 | 480
Lower Ground | 14 | 420
Electrical | 13 | 390
Ground | 9 | 270
TOTAL | 175 | 5250

## By Cable Type
Cable type | Count | Total length (m)
4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 98 | 2940
4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 34 | 1020
Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 27 | 810
4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 16 | 480

## Detail (cables)
ID | From | To | Cable type | Length (m) | Status | Corrected (m) | Verified by | Date | Drawing ref | Notes
C0001 | PNL-AHU-L2 | AHU-2M.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0002 | PNL-AHU-L2 | AHU-2M.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0003 | PNL-AHU-L2 | AHU-2M.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0004 | PNL-AHU-L2 | AHU-2M.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0005 | PNL-AHU-L2 | AHU-2M.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0006 | PNL-AHU-L2 | AHU-2M.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0007 | PNL-CH-PLANT-GND | CH-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0008 | PNL-CH-PLANT-GND | CH-1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0009 | PNL-CH-PLANT-GND | CH-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0010 | PNL-CH-PLANT-GND | CH-2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0011 | PNL-CH-PLANT-GND | CH-3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0012 | PNL-CH-PLANT-GND | CH-3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0013 | PNL-CHWP-GND | CHWP-1.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0014 | PNL-CHWP-GND | CHWP-1.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0015 | PNL-CHWP-GND | CHWP-1.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0016 | PNL-CHWP-GND | CHWP-1.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0017 | PNL-CHWP-GND | CHWP-1.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0018 | PNL-CHWP-GND | CHWP-1.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0019 | PNL-CHWP-GND | CHWP-1.3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0020 | PNL-CHWP-GND | CHWP-1.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0021 | PNL-CHWP-GND | CHWP-1.3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0022 | PNL-CHWP-L2 | COMP-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0023 | PNL-CHWP-L2 | COMP-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0024 | PNL-CHWP-L2 | COMP-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0025 | PNL-CT-RD | CT-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0026 | PNL-CT-RD | CT-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0027 | PNL-CT-RD | CT-1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0028 | PNL-CT-RD | CT-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0029 | PNL-CT-RD | CT-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0030 | PNL-CT-RD | CT-2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0031 | PNL-CT-RD | CT-3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0032 | PNL-CT-RD | CT-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0033 | PNL-CT-RD | CT-3 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0034 | PNL-CT-RD | CT-COMMON (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0035 | PNL-DOAS-L2 | DOAS-2W (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0036 | PNL-DOAS-L2 | DOAS-2W (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0037 | PNL-DOAS-L2 | DOAS-2W (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0038 | PNL-DOAS-RD | DOAS-RD.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0039 | PNL-DOAS-RD | DOAS-RD.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0040 | PNL-DOAS-RD | DOAS-RD.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0041 | PNL-DOAS-RD | DOAS-RD.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0042 | PNL-DOAS-RD | DOAS-RD.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0043 | PNL-DOAS-RD | DOAS-RD.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0044 | PNL-VENT-RD | EF-1 (RD) (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0045 | PNL-VENT-GF | EF-1.2A (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0046 | PNL-VENT-GF | EF-1MR.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0047 | PNL-VENT-GF | EF-1ST0.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0048 | PNL-VENT-L2 | EF-2.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0049 | PNL-VENT-L2 | EF-2.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0050 | PNL-VENT-L2 | EF-2.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0051 | PNL-VENT-L2 | EF-2.4 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0052 | PNL-VENT-L2 | EF-2B.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0053 | PNL-VENT-L2 | EF-2B.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0054 | PNL-VENT-L3 | EF-3.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0055 | PNL-VENT-L3 | EF-3.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0056 | PNL-VENT-BSMT | EF-3SF.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0057 | PNL-VENT-BSMT | EF-8R.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0058 | PNL-VENT-BSMT | EF-B.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0059 | PNL-VENT-BSMT | EF-B.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0060 | PNL-VENT-BSMT | EF-BS.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0061 | PNL-VENT-BSMT | EF-BS.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0062 | PNL-VENT-L2 | EF-CHR.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0063 | PNL-VENT-L2 | EF-CHR.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0064 | PNL-VENT-BSMT | EF-GLZ.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0065 | PNL-VENT-BSMT | EF-GLZ.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0066 | PNL-VENT-L2 | EF-GS.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0067 | PNL-VENT-L2 | EF-GS.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0068 | PNL-VENT-BSMT | EF-HP.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0069 | PNL-VENT-GF | EF-LPG.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0070 | PNL-VENT-BSMT | EF-MC.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0071 | PNL-VENT-BSMT | EF-MFP.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0072 | PNL-VENT-GF | EF-MRF.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0073 | PNL-VENT-BSMT | EF-PR.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0074 | PNL-VENT-BSMT | EF-PR.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0075 | PNL-VENT-RD | EF-RD.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0076 | PNL-VENT-RD | EF-RD.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0077 | PNL-VENT-BSMT | EF-RR.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0078 | PNL-CHWP-L2 | HDR-CHW-BP (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0079 | PNL-CHWP-L2 | HDR-CHWR (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0080 | PNL-CHWP-L2 | HDR-CHWS (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0081 | PNL-CT-RD | HDR-CWR-RD (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0082 | PNL-CT-RD | HDR-CWS-RD (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0083 | PNL-PL-HZ | HDR-HW-HZ (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0084 | PNL-PL-LZ | HDR-HW-LZ (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0085 | PNL-PL-LZ | HP-LZ-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0086 | PNL-PL-LZ | HP-LZ-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0087 | PNL-PL-LZ | HP-LZ-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0088 | PNL-PL-HZ | HWT-HZ-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0089 | PNL-PL-HZ | HWT-HZ-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0090 | PNL-PL-HZ | HWT-HZ-3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0091 | PNL-PL-LZ | HWT-LZ-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0092 | PNL-PL-LZ | HWT-LZ-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0093 | PNL-PL-LZ | HWT-LZ-3 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0094 | PNL-AHU-L2 | OZ-2M.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0095 | PNL-AHU-L2 | OZ-2M.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0096 | PNL-AHU-L2 | OZ-2M.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0097 | PNL-AHU-L2 | OZ-2M.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0098 | PNL-PAHU-RD | PAHU-RD.1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0099 | PNL-PAHU-RD | PAHU-RD.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0100 | PNL-PAHU-RD | PAHU-RD.1 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0101 | PNL-PAHU-RD | PAHU-RD.2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0102 | PNL-PAHU-RD | PAHU-RD.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0103 | PNL-PAHU-RD | PAHU-RD.2 (ME Contractor) | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 30 | unverified
C0104 | PNL-CHWP-L2 | PCHWP-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0105 | PNL-CHWP-L2 | PCHWP-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0106 | PNL-CHWP-L2 | PCHWP-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0107 | PNL-CHWP-L2 | PCHWP-4 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0108 | PNL-PL-LZ | RP-LZ-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0109 | PNL-PL-LZ | RP-LZ-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0110 | PNL-PL-LZ | RP-LZ-3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0111 | PNL-BL-LZ | SB-1 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0112 | PNL-BL-LZ | SB-1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0113 | PNL-BL-LZ | SB-2 (BMS Contractor) | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 30 | unverified
C0114 | PNL-BL-LZ | SB-2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0115 | PNL-VENT-GF | TEF-1.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0116 | PNL-VENT-GF | TEF-1.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0117 | PNL-VENT-GF | TEF-1.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0118 | PNL-VENT-GF | TEF-1.4 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0119 | PNL-VENT-L2 | TEF-2.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0120 | PNL-VENT-L2 | TEF-2.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0121 | PNL-VENT-L2 | TEF-2B.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0122 | PNL-VENT-L3 | TEF-3A.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0123 | PNL-VENT-L3 | TEF-3A.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0124 | PNL-VENT-L3 | TEF-3B (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0125 | PNL-VENT-L3 | TEF-3C.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0126 | PNL-VENT-L3 | TEF-3C.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0127 | PNL-VENT-L3 | TEF-3D.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0128 | PNL-VENT-L3 | TEF-3D.10 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0129 | PNL-VENT-L3 | TEF-3D.11 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0130 | PNL-VENT-L3 | TEF-3D.12 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0131 | PNL-VENT-L3 | TEF-3D.13 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0132 | PNL-VENT-L3 | TEF-3D.14 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0133 | PNL-VENT-L3 | TEF-3D.15 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0134 | PNL-VENT-L3 | TEF-3D.16 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0135 | PNL-VENT-L3 | TEF-3D.17 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0136 | PNL-VENT-L3 | TEF-3D.18 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0137 | PNL-VENT-L3 | TEF-3D.19 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0138 | PNL-VENT-L3 | TEF-3D.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0139 | PNL-VENT-L3 | TEF-3D.20 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0140 | PNL-VENT-L3 | TEF-3D.3 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0141 | PNL-VENT-L3 | TEF-3D.4 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0142 | PNL-VENT-L3 | TEF-3D.5 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0143 | PNL-VENT-L3 | TEF-3D.6 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0144 | PNL-VENT-L3 | TEF-3D.7 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0145 | PNL-VENT-L3 | TEF-3D.8 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0146 | PNL-VENT-L3 | TEF-3D.9 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0147 | PNL-VENT-BSMT | TEF-B.1 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0148 | PNL-VENT-BSMT | TEF-B.2 (Equipment Supplier) | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 30 | unverified
C0149 | PNL-CH-PLANT-GND | CH-1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0150 | PNL-CH-PLANT-GND | CH-2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0151 | PNL-CH-PLANT-GND | CH-3 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0152 | PNL-CHWP-L2 | BTU-CHWS-MAIN (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0153 | PNL-CHWP-GND | CHWP-1.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0154 | PNL-CHWP-GND | CHWP-1.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0155 | PNL-CHWP-GND | CHWP-1.3 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0156 | PNL-DOAS-L2 | DOAS-2W (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0157 | PNL-DOAS-RD | DOAS-RD.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0158 | PNL-DOAS-RD | DOAS-RD.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0159 | PNL-AHU-L2 | AHU-2M.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0160 | PNL-AHU-L2 | AHU-2M.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0161 | PNL-PAHU-RD | PAHU-RD.1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0162 | PNL-PAHU-RD | PAHU-RD.2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0163 | PNL-EE-MAIN | MTR-MAIN-1 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0164 | PNL-EE-MAIN | MTR-MAIN-2 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0165 | PNL-EE-MAIN | MTR-MAIN-3 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0166 | PNL-EE-DIST | MTR-FDR-01 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0167 | PNL-EE-DIST | MTR-FDR-02 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0168 | PNL-EE-DIST | MTR-FDR-03 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0169 | PNL-EE-DIST | MTR-FDR-04 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0170 | PNL-EE-DIST | MTR-FDR-05 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0171 | PNL-EE-DIST | MTR-FDR-06 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0172 | PNL-EE-DIST | MTR-FDR-07 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0173 | PNL-EE-DIST | MTR-FDR-08 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0174 | PNL-EE-DIST | MTR-FDR-09 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
C0175 | PNL-EE-DIST | MTR-FDR-10 (Network) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 30 | unverified
T0176 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0177 | BMS Server Room (head-end) | All BMS panels at 3rd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0178 | BMS Server Room (head-end) | All BMS panels at Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0179 | BMS Server Room (head-end) | All BMS panels at Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0180 | BMS Server Room (head-end) | All BMS panels at Lower Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0181 | BMS Server Room (head-end) | All BMS panels at Roofdeck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | unverified
T0182 | BMS Server Room (head-end) | All BMS panel controllers (MS/TP daisy-chain or branched) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 540 | unverified
P0183 | Local panelboard / EE-supplied feeder | PNL-AHU-L2 — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0184 | Local panelboard / EE-supplied feeder | PNL-BL-LZ — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0185 | Local panelboard / EE-supplied feeder | PNL-CH-PLANT-GND — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0186 | Local panelboard / EE-supplied feeder | PNL-CHWP-GND — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0187 | Local panelboard / EE-supplied feeder | PNL-CHWP-L2 — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0188 | Local panelboard / EE-supplied feeder | PNL-CT-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0189 | Local panelboard / EE-supplied feeder | PNL-DOAS-L2 — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0190 | Local panelboard / EE-supplied feeder | PNL-DOAS-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0191 | Local panelboard / EE-supplied feeder | PNL-EE-DIST — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0192 | Local panelboard / EE-supplied feeder | PNL-EE-MAIN — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0193 | Local panelboard / EE-supplied feeder | PNL-PAHU-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0194 | Local panelboard / EE-supplied feeder | PNL-PL-HZ — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0195 | Local panelboard / EE-supplied feeder | PNL-PL-LZ — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0196 | Local panelboard / EE-supplied feeder | PNL-VENT-BSMT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0197 | Local panelboard / EE-supplied feeder | PNL-VENT-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0198 | Local panelboard / EE-supplied feeder | PNL-VENT-L2 — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0199 | Local panelboard / EE-supplied feeder | PNL-VENT-L3 — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified
P0200 | Local panelboard / EE-supplied feeder | PNL-VENT-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | unverified

## Verification schema
How to record verification / corrections in A3-cable-schedule.yaml
Find the affected row in the YAML by ID (Detail sheet column A) and add a verification: block:
- id: C0001
from: PNL-CH-PLANT-GND
to: CH-1 (BMS Contractor)
cable_type: 4C × 1.5 mm² shielded FRLS
length_m: 30
verification: # ADDED by team
status: needs_correction # unverified ¦ verified ¦ needs_correction ¦ uncertain
corrected_length_m: 42 # team's measured / confirmed value
verified_by: J. Cruz
verified_date: 2026-05-10
drawing_ref: "EE-09 grid B-2"
notes: ""
After saving, re-run: python3 _playbook/tools/generate-deliverables.py <project>
Corrections propagate to B4 manhours, BOQ, and final deliverables automatically.
Recommended verification methods (priority order):
1. Site walkthrough with measurement (most accurate; for cable lengths, after structural completion).
2. Properly-scaled architectural drawings.
3. Mechanical contractor's tray layout combined with BMS panel locations.
4. A-001 default with ±20% contingency in BOQ — last resort.