## Summary
A1 — Consolidated I/O List Summary
Project | Kingsford Hotel Bacolod BMS
Total I/O rows | 716
By type
DI | 348
HLI | 166
AI | 126
AO | 29
Network | 27
DO | 20
By C/O
Equipment Supplier | 447
BMS Contractor | 215
ME Contractor | 54
By system
General Ventilation | 204
Chilled Water | 159
Power Metering | 78
DOAS - Hotel/Roofdeck | 52
BOH Air Handling | 51
Plumbing & Sanitary Hotwater | 48
Boiler/Laundry | 32
AHU - Casino | 32
PAHU - Roofdeck | 28
DOAS - Casino MVAC | 26
AHU - Casino (Ozonizer) | 6
By panel
PNL-CH-PLANT-GND | 84
PNL-VENT-L3 | 81
PNL-EE-DIST | 60
PNL-DOAS-RD | 52
PNL-CHWP-GND | 51
PNL-VENT-BSMT | 48
PNL-CHWP-L2 | 44
PNL-VENT-L2 | 39
PNL-AHU-L2 | 38
PNL-BL-LZ | 32
PNL-CT-RD | 31
PNL-PAHU-RD | 28
PNL-VENT-GF | 27
PNL-DOAS-L2 | 26
PNL-PL-LZ | 24
PNL-PL-HZ | 24
PNL-EE-MAIN | 18
PNL-VENT-RD | 9

## All IO Points
ID | System | Equipment Class | Equipment Instance | Location | Point Description | Type | Field Device | C/O | DoO Ref | Panel | Source | Notes
chws.ch-1.network | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | BACnet/IP gateway from chiller controller | Network | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-1..36 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | 1 network drop per chiller; chiller native BACnet
chws.ch-1.entering-chw-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Entering Chilled Water Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | BMS-03/Package Water Chiller P&ID/MR-11 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-1.leaving-chw-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Leaving Chilled Water Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | BMS-03/Package Water Chiller P&ID/MR-12 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-1.entering-cw-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Entering Condenser Water Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | BMS-03/Package Water Chiller P&ID/MR-21 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-1.leaving-cw-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Leaving Condenser Water Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | BMS-03/Package Water Chiller P&ID/MR-22 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-1.chw-supply-flow | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Chilled Water Supply Flow Metering | AI | Flow Sensor (insertion or in-line) | BMS Contractor | BMS-03/Package Water Chiller P&ID | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Per-chiller branch flow
chws.ch-1.chw-return-flow | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Chilled Water Return Flow Metering | AI | Flow Sensor (insertion or in-line) | BMS Contractor | BMS-03/Package Water Chiller P&ID | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Per-chiller branch flow
chws.ch-1.cw-supply-flow | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Condenser Water Supply Flow Metering | AI | Flow Sensor (insertion or in-line) | BMS Contractor | BMS-03/Package Water Chiller P&ID | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Per-chiller condenser branch flow
chws.ch-1.iso-vlv-chw-rs | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Isolation Motorized Valve Status — CHW Return & Supply | DI | Electric Valve Actuator (limit switch) | ME Contractor | BMS-03/Package Water Chiller P&ID/MR-9 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Valves supplied by ME; status DI to BMS
chws.ch-1.iso-vlv-cw-rs | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Isolation Motorized Valve Status — COW Return & Supply | DI | Electric Valve Actuator (limit switch) | ME Contractor | BMS-03/Package Water Chiller P&ID/MR-10 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Valves supplied by ME; status DI to BMS
chws.ch-1.evap-approach-dt | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Evaporator Approach Delta Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-13 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet; sub-point of chws.ch-1.network
chws.ch-1.evap-approach-dp | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Evaporator Approach Delta Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-14 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.evap-refrig-press | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Evaporator Refrigerant Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-15 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.evap-refrig-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Evaporator Refrigerant Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-16 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.cond-refrig-press | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Condenser Refrigerant Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-17 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.cond-refrig-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Condenser Refrigerant Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-18 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.cond-approach-dt | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Condenser Approach Delta Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-19 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.cond-approach-dp | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Condenser Approach Delta Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-20 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.oil-sump-press | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Oil Sump Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-7 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.oil-sump-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Oil Sump Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-8 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.oil-pump-status | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Oil Pump Status (ON/OFF) | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-6 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.oil-pump-trip | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Oil Pump Trip Status | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/Alarm-2 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.compressor-onoff | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Chiller Compressor Pump On/Off Status | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-1 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.compressor-hoa | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Chiller Compressor Hand/Off/Auto Status | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-2 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.compressor-trip | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Chiller Compressor Trip Alarm Status | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/Alarm-1 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.motor-load-current | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Motor Load Current | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-3 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.motor-consumption | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Motor Consumption (KW-Hr / BTU Monitoring) | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-4 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-1.winding-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-1 | GND/Chiller Plant Room | Winding Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-5 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.network | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | BACnet/IP gateway from chiller controller | Network | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-1..36 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-2.entering-chw-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Entering Chilled Water Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | BMS-03/Package Water Chiller P&ID/MR-11 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-2.leaving-chw-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Leaving Chilled Water Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | BMS-03/Package Water Chiller P&ID/MR-12 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-2.entering-cw-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Entering Condenser Water Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | BMS-03/Package Water Chiller P&ID/MR-21 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-2.leaving-cw-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Leaving Condenser Water Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | BMS-03/Package Water Chiller P&ID/MR-22 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-2.chw-supply-flow | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Chilled Water Supply Flow Metering | AI | Flow Sensor (insertion or in-line) | BMS Contractor | BMS-03/Package Water Chiller P&ID | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Per-chiller branch flow
chws.ch-2.chw-return-flow | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Chilled Water Return Flow Metering | AI | Flow Sensor (insertion or in-line) | BMS Contractor | BMS-03/Package Water Chiller P&ID | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Per-chiller branch flow
chws.ch-2.cw-supply-flow | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Condenser Water Supply Flow Metering | AI | Flow Sensor (insertion or in-line) | BMS Contractor | BMS-03/Package Water Chiller P&ID | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Per-chiller condenser branch flow
chws.ch-2.iso-vlv-chw-rs | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Isolation Motorized Valve Status — CHW Return & Supply | DI | Electric Valve Actuator (limit switch) | ME Contractor | BMS-03/Package Water Chiller P&ID/MR-9 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Valves supplied by ME; status DI to BMS
chws.ch-2.iso-vlv-cw-rs | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Isolation Motorized Valve Status — COW Return & Supply | DI | Electric Valve Actuator (limit switch) | ME Contractor | BMS-03/Package Water Chiller P&ID/MR-10 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Valves supplied by ME; status DI to BMS
chws.ch-2.evap-approach-dt | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Evaporator Approach Delta Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-13 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.evap-approach-dp | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Evaporator Approach Delta Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-14 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.evap-refrig-press | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Evaporator Refrigerant Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-15 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.evap-refrig-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Evaporator Refrigerant Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-16 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.cond-refrig-press | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Condenser Refrigerant Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-17 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.cond-refrig-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Condenser Refrigerant Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-18 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.cond-approach-dt | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Condenser Approach Delta Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-19 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.cond-approach-dp | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Condenser Approach Delta Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-20 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.oil-sump-press | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Oil Sump Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-7 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.oil-sump-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Oil Sump Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-8 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.oil-pump-status | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Oil Pump Status (ON/OFF) | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-6 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.oil-pump-trip | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Oil Pump Trip Status | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/Alarm-2 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.compressor-onoff | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Chiller Compressor Pump On/Off Status | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-1 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.compressor-hoa | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Chiller Compressor Hand/Off/Auto Status | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-2 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.compressor-trip | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Chiller Compressor Trip Alarm Status | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/Alarm-1 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.motor-load-current | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Motor Load Current | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-3 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.motor-consumption | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Motor Consumption (KW-Hr / BTU Monitoring) | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-4 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-2.winding-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-2 | GND/Chiller Plant Room | Winding Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-5 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.network | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | BACnet/IP gateway from chiller controller | Network | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-1..36 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-3.entering-chw-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Entering Chilled Water Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | BMS-03/Package Water Chiller P&ID/MR-11 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-3.leaving-chw-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Leaving Chilled Water Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | BMS-03/Package Water Chiller P&ID/MR-12 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-3.entering-cw-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Entering Condenser Water Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | BMS-03/Package Water Chiller P&ID/MR-21 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-3.leaving-cw-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Leaving Condenser Water Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | BMS-03/Package Water Chiller P&ID/MR-22 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room
chws.ch-3.chw-supply-flow | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Chilled Water Supply Flow Metering | AI | Flow Sensor (insertion or in-line) | BMS Contractor | BMS-03/Package Water Chiller P&ID | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Per-chiller branch flow
chws.ch-3.chw-return-flow | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Chilled Water Return Flow Metering | AI | Flow Sensor (insertion or in-line) | BMS Contractor | BMS-03/Package Water Chiller P&ID | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Per-chiller branch flow
chws.ch-3.cw-supply-flow | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Condenser Water Supply Flow Metering | AI | Flow Sensor (insertion or in-line) | BMS Contractor | BMS-03/Package Water Chiller P&ID | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Per-chiller condenser branch flow
chws.ch-3.iso-vlv-chw-rs | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Isolation Motorized Valve Status — CHW Return & Supply | DI | Electric Valve Actuator (limit switch) | ME Contractor | BMS-03/Package Water Chiller P&ID/MR-9 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Valves supplied by ME; status DI to BMS
chws.ch-3.iso-vlv-cw-rs | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Isolation Motorized Valve Status — COW Return & Supply | DI | Electric Valve Actuator (limit switch) | ME Contractor | BMS-03/Package Water Chiller P&ID/MR-10 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Valves supplied by ME; status DI to BMS
chws.ch-3.evap-approach-dt | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Evaporator Approach Delta Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-13 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.evap-approach-dp | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Evaporator Approach Delta Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-14 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.evap-refrig-press | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Evaporator Refrigerant Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-15 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.evap-refrig-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Evaporator Refrigerant Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-16 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.cond-refrig-press | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Condenser Refrigerant Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-17 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.cond-refrig-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Condenser Refrigerant Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-18 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.cond-approach-dt | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Condenser Approach Delta Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-19 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.cond-approach-dp | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Condenser Approach Delta Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-20 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.oil-sump-press | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Oil Sump Pressure | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-7 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.oil-sump-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Oil Sump Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-8 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.oil-pump-status | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Oil Pump Status (ON/OFF) | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-6 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.oil-pump-trip | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Oil Pump Trip Status | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/Alarm-2 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.compressor-onoff | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Chiller Compressor Pump On/Off Status | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-1 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.compressor-hoa | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Chiller Compressor Hand/Off/Auto Status | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-2 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.compressor-trip | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Chiller Compressor Trip Alarm Status | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/Alarm-1 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.motor-load-current | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Motor Load Current | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-3 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.motor-consumption | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Motor Consumption (KW-Hr / BTU Monitoring) | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-4 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.ch-3.winding-temp | Chilled Water | Chiller (Package Water-Cooled) | CH-3 | GND/Chiller Plant Room | Winding Temperature | HLI | - | Equipment Supplier | BMS-03/Package Water Chiller P&ID/MR-5 | PNL-CH-PLANT-GND | BMS-01:r0c1; MC-ME:Chiller Room | Via chiller BACnet
chws.pchwp-1.run-status | Chilled Water | Primary CHW Pump | PCHWP-1 | 2F/CHW Pump Room | On/Off Status (run feedback) | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/MR-1 | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-1.hoa | Chilled Water | Primary CHW Pump | PCHWP-1 | 2F/CHW Pump Room | Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Primary CHW & CW P&ID | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-1.trip | Chilled Water | Primary CHW Pump | PCHWP-1 | 2F/CHW Pump Room | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/Alarm-1 | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-1.vfd-speed-fb | Chilled Water | Primary CHW Pump | PCHWP-1 | 2F/CHW Pump Room | Variable Speed Monitoring (VFD speed feedback) | AI | VFD | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/MR-2 | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-1.vfd-speed-cmd | Chilled Water | Primary CHW Pump | PCHWP-1 | 2F/CHW Pump Room | VFD Speed Command (modulating start/stop/speed) | AO | VFD | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/Turn ON/OFF | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps | Or HLI if VFD has BACnet
chws.pchwp-2.run-status | Chilled Water | Primary CHW Pump | PCHWP-2 | 2F/CHW Pump Room | On/Off Status (run feedback) | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/MR-1 | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-2.hoa | Chilled Water | Primary CHW Pump | PCHWP-2 | 2F/CHW Pump Room | Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Primary CHW & CW P&ID | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-2.trip | Chilled Water | Primary CHW Pump | PCHWP-2 | 2F/CHW Pump Room | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/Alarm-1 | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-2.vfd-speed-fb | Chilled Water | Primary CHW Pump | PCHWP-2 | 2F/CHW Pump Room | Variable Speed Monitoring (VFD speed feedback) | AI | VFD | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/MR-2 | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-2.vfd-speed-cmd | Chilled Water | Primary CHW Pump | PCHWP-2 | 2F/CHW Pump Room | VFD Speed Command | AO | VFD | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/Turn ON/OFF | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-3.run-status | Chilled Water | Primary CHW Pump | PCHWP-3 | 2F/CHW Pump Room | On/Off Status (run feedback) | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/MR-1 | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-3.hoa | Chilled Water | Primary CHW Pump | PCHWP-3 | 2F/CHW Pump Room | Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Primary CHW & CW P&ID | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-3.trip | Chilled Water | Primary CHW Pump | PCHWP-3 | 2F/CHW Pump Room | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/Alarm-1 | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-3.vfd-speed-fb | Chilled Water | Primary CHW Pump | PCHWP-3 | 2F/CHW Pump Room | Variable Speed Monitoring (VFD speed feedback) | AI | VFD | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/MR-2 | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-3.vfd-speed-cmd | Chilled Water | Primary CHW Pump | PCHWP-3 | 2F/CHW Pump Room | VFD Speed Command | AO | VFD | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/Turn ON/OFF | PNL-CHWP-L2 | BMS-03:r0c0; MC-ME:Primary CHW Pumps
chws.pchwp-4.run-status | Chilled Water | Primary CHW Pump (Standby) | PCHWP-4 | 2F/CHW Pump Room | On/Off Status (run feedback) | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/MR-1 | PNL-CHWP-L2 | MC-ME:Primary CHW Pumps; A-CHW-001 | Standby pump assumed; refine count after Q-005/Q-008
chws.pchwp-4.hoa | Chilled Water | Primary CHW Pump (Standby) | PCHWP-4 | 2F/CHW Pump Room | Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Primary CHW & CW P&ID | PNL-CHWP-L2 | MC-ME:Primary CHW Pumps; A-CHW-001
chws.pchwp-4.trip | Chilled Water | Primary CHW Pump (Standby) | PCHWP-4 | 2F/CHW Pump Room | Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/Alarm-1 | PNL-CHWP-L2 | MC-ME:Primary CHW Pumps; A-CHW-001
chws.pchwp-4.vfd-speed-fb | Chilled Water | Primary CHW Pump (Standby) | PCHWP-4 | 2F/CHW Pump Room | Variable Speed Monitoring | AI | VFD | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/MR-2 | PNL-CHWP-L2 | MC-ME:Primary CHW Pumps; A-CHW-001
chws.pchwp-4.vfd-speed-cmd | Chilled Water | Primary CHW Pump (Standby) | PCHWP-4 | 2F/CHW Pump Room | VFD Speed Command | AO | VFD | Equipment Supplier | BMS-03/Primary CHW & CW P&ID/Turn ON/OFF | PNL-CHWP-L2 | MC-ME:Primary CHW Pumps; A-CHW-001
chws.comp-1.run-status | Chilled Water | Condenser Water Pump | COMP-1 | 2F/CHW Pump Room | Pump Motor Start/Stop Control feedback (On/Off Status) | DI | Auxiliary Contact | Equipment Supplier | BMS-03/CW Pump P&ID/MR-1 | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:Condenser Water Pumps
chws.comp-1.hoa | Chilled Water | Condenser Water Pump | COMP-1 | 2F/CHW Pump Room | Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/CW Pump P&ID/MR-2 | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:Condenser Water Pumps
chws.comp-1.trip | Chilled Water | Condenser Water Pump | COMP-1 | 2F/CHW Pump Room | Pump Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | BMS-03/CW Pump P&ID/Alarm-1 | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:Condenser Water Pumps
chws.comp-1.start-cmd | Chilled Water | Condenser Water Pump | COMP-1 | 2F/CHW Pump Room | Start/Stop Control | DO | Contactor relay | Equipment Supplier | BMS-03/CW Pump P&ID/Turn ON/OFF | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:Condenser Water Pumps | BMS commands pump start sequenced with chiller
chws.comp-2.run-status | Chilled Water | Condenser Water Pump | COMP-2 | 2F/CHW Pump Room | Pump Motor Start/Stop Control feedback (On/Off Status) | DI | Auxiliary Contact | Equipment Supplier | BMS-03/CW Pump P&ID/MR-1 | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:Condenser Water Pumps
chws.comp-2.hoa | Chilled Water | Condenser Water Pump | COMP-2 | 2F/CHW Pump Room | Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/CW Pump P&ID/MR-2 | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:Condenser Water Pumps
chws.comp-2.trip | Chilled Water | Condenser Water Pump | COMP-2 | 2F/CHW Pump Room | Pump Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | BMS-03/CW Pump P&ID/Alarm-1 | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:Condenser Water Pumps
chws.comp-2.start-cmd | Chilled Water | Condenser Water Pump | COMP-2 | 2F/CHW Pump Room | Start/Stop Control | DO | Contactor relay | Equipment Supplier | BMS-03/CW Pump P&ID/Turn ON/OFF | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:Condenser Water Pumps
chws.comp-3.run-status | Chilled Water | Condenser Water Pump | COMP-3 | 2F/CHW Pump Room | Pump Motor Start/Stop Control feedback (On/Off Status) | DI | Auxiliary Contact | Equipment Supplier | BMS-03/CW Pump P&ID/MR-1 | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:Condenser Water Pumps
chws.comp-3.hoa | Chilled Water | Condenser Water Pump | COMP-3 | 2F/CHW Pump Room | Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/CW Pump P&ID/MR-2 | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:Condenser Water Pumps
chws.comp-3.trip | Chilled Water | Condenser Water Pump | COMP-3 | 2F/CHW Pump Room | Pump Trip Alarm | DI | Auxiliary Contact | Equipment Supplier | BMS-03/CW Pump P&ID/Alarm-1 | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:Condenser Water Pumps
chws.comp-3.start-cmd | Chilled Water | Condenser Water Pump | COMP-3 | 2F/CHW Pump Room | Start/Stop Control | DO | Contactor relay | Equipment Supplier | BMS-03/CW Pump P&ID/Turn ON/OFF | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:Condenser Water Pumps
chws.ct-1.fan-status | Chilled Water | Cooling Tower | CT-1 | Roofdeck/Cooling Tower Area | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Cooling Tower P&ID/MR-1 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-1.fan-trip | Chilled Water | Cooling Tower | CT-1 | Roofdeck/Cooling Tower Area | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Cooling Tower P&ID/Alarm-1 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-1.fan-start-cmd | Chilled Water | Cooling Tower | CT-1 | Roofdeck/Cooling Tower Area | Fan Motor Start/Stop Command | DO | Contactor relay | Equipment Supplier | BMS-03/Cooling Tower P&ID/Turn ON/OFF | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower | Sequenced with COW pump and chiller
chws.ct-1.basin-level-low | Chilled Water | Cooling Tower | CT-1 | Roofdeck/Cooling Tower Area | Level Alarm Low (CT Basin) | DI | Level Sensor / Electrode | BMS Contractor | BMS-03/Cooling Tower P&ID/Alarm-2 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-1.basin-level-high | Chilled Water | Cooling Tower | CT-1 | Roofdeck/Cooling Tower Area | Level Alarm High (CT Basin) | DI | Level Sensor / Electrode | BMS Contractor | BMS-03/Cooling Tower P&ID/Alarm-2 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-1.iso-vlv-cw-rs | Chilled Water | Cooling Tower | CT-1 | Roofdeck/Cooling Tower Area | Isolation Motorized Valve Status — COW R&S | DI | Electric Valve Actuator | ME Contractor | BMS-03/Cooling Tower P&ID/MR-12 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-1.blowdown-vlv-cmd | Chilled Water | Cooling Tower | CT-1 | Roofdeck/Cooling Tower Area | Motorized Blowdown Valve Control | DO | Electric Valve Actuator | BMS Contractor | BMS-03/Cooling Tower P&ID/Turn ON/OFF blowdown | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-1.blowdown-vlv-stat | Chilled Water | Cooling Tower | CT-1 | Roofdeck/Cooling Tower Area | Motorized Blowdown Valve Status | DI | Electric Valve Actuator | BMS Contractor | BMS-03/Cooling Tower P&ID/MR-14 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-1.blowdown-ph | Chilled Water | Cooling Tower | CT-1 | Roofdeck/Cooling Tower Area | Blowdown Corrosion/Scale Monitoring (pH/Conductivity) | AI | pH Sensor / Conductivity Sensor | ME Contractor | BMS-03/Cooling Tower P&ID/MR-13 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower | Field device by ME; signal to BMS
chws.ct-2.fan-status | Chilled Water | Cooling Tower | CT-2 | Roofdeck/Cooling Tower Area | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Cooling Tower P&ID/MR-1 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-2.fan-trip | Chilled Water | Cooling Tower | CT-2 | Roofdeck/Cooling Tower Area | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Cooling Tower P&ID/Alarm-1 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-2.fan-start-cmd | Chilled Water | Cooling Tower | CT-2 | Roofdeck/Cooling Tower Area | Fan Motor Start/Stop Command | DO | Contactor relay | Equipment Supplier | BMS-03/Cooling Tower P&ID/Turn ON/OFF | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-2.basin-level-low | Chilled Water | Cooling Tower | CT-2 | Roofdeck/Cooling Tower Area | Level Alarm Low (CT Basin) | DI | Level Sensor / Electrode | BMS Contractor | BMS-03/Cooling Tower P&ID/Alarm-2 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-2.basin-level-high | Chilled Water | Cooling Tower | CT-2 | Roofdeck/Cooling Tower Area | Level Alarm High (CT Basin) | DI | Level Sensor / Electrode | BMS Contractor | BMS-03/Cooling Tower P&ID/Alarm-2 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-2.iso-vlv-cw-rs | Chilled Water | Cooling Tower | CT-2 | Roofdeck/Cooling Tower Area | Isolation Motorized Valve Status — COW R&S | DI | Electric Valve Actuator | ME Contractor | BMS-03/Cooling Tower P&ID/MR-12 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-2.blowdown-vlv-cmd | Chilled Water | Cooling Tower | CT-2 | Roofdeck/Cooling Tower Area | Motorized Blowdown Valve Control | DO | Electric Valve Actuator | BMS Contractor | BMS-03/Cooling Tower P&ID/Turn ON/OFF blowdown | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-2.blowdown-vlv-stat | Chilled Water | Cooling Tower | CT-2 | Roofdeck/Cooling Tower Area | Motorized Blowdown Valve Status | DI | Electric Valve Actuator | BMS Contractor | BMS-03/Cooling Tower P&ID/MR-14 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-2.blowdown-ph | Chilled Water | Cooling Tower | CT-2 | Roofdeck/Cooling Tower Area | Blowdown Corrosion/Scale Monitoring | AI | pH Sensor / Conductivity Sensor | ME Contractor | BMS-03/Cooling Tower P&ID/MR-13 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-3.fan-status | Chilled Water | Cooling Tower | CT-3 | Roofdeck/Cooling Tower Area | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Cooling Tower P&ID/MR-1 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-3.fan-trip | Chilled Water | Cooling Tower | CT-3 | Roofdeck/Cooling Tower Area | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | BMS-03/Cooling Tower P&ID/Alarm-1 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-3.fan-start-cmd | Chilled Water | Cooling Tower | CT-3 | Roofdeck/Cooling Tower Area | Fan Motor Start/Stop Command | DO | Contactor relay | Equipment Supplier | BMS-03/Cooling Tower P&ID/Turn ON/OFF | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-3.basin-level-low | Chilled Water | Cooling Tower | CT-3 | Roofdeck/Cooling Tower Area | Level Alarm Low (CT Basin) | DI | Level Sensor / Electrode | BMS Contractor | BMS-03/Cooling Tower P&ID/Alarm-2 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-3.basin-level-high | Chilled Water | Cooling Tower | CT-3 | Roofdeck/Cooling Tower Area | Level Alarm High (CT Basin) | DI | Level Sensor / Electrode | BMS Contractor | BMS-03/Cooling Tower P&ID/Alarm-2 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-3.iso-vlv-cw-rs | Chilled Water | Cooling Tower | CT-3 | Roofdeck/Cooling Tower Area | Isolation Motorized Valve Status — COW R&S | DI | Electric Valve Actuator | ME Contractor | BMS-03/Cooling Tower P&ID/MR-12 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-3.blowdown-vlv-cmd | Chilled Water | Cooling Tower | CT-3 | Roofdeck/Cooling Tower Area | Motorized Blowdown Valve Control | DO | Electric Valve Actuator | BMS Contractor | BMS-03/Cooling Tower P&ID/Turn ON/OFF blowdown | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-3.blowdown-vlv-stat | Chilled Water | Cooling Tower | CT-3 | Roofdeck/Cooling Tower Area | Motorized Blowdown Valve Status | DI | Electric Valve Actuator | BMS Contractor | BMS-03/Cooling Tower P&ID/MR-14 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-3.blowdown-ph | Chilled Water | Cooling Tower | CT-3 | Roofdeck/Cooling Tower Area | Blowdown Corrosion/Scale Monitoring | AI | pH Sensor / Conductivity Sensor | ME Contractor | BMS-03/Cooling Tower P&ID/MR-13 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.ct-common.outside-air-temp | Chilled Water | Cooling Tower (Common) | CT-COMMON | Roofdeck/Cooling Tower Area | Outside Air Temperature Monitoring | AI | Temperature Sensor (outdoor) | BMS Contractor | BMS-03/Cooling Tower P&ID/MR-4 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower | Single OA sensor serves all CTs
chws.ct-common.outside-air-rh | Chilled Water | Cooling Tower (Common) | CT-COMMON | Roofdeck/Cooling Tower Area | Outside Air Humidity Monitoring | AI | Humidity Sensor (outdoor) | BMS Contractor | BMS-03/Cooling Tower P&ID/MR-5 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower | Single OA RH sensor serves all CTs
chws.hdr-cws-rd.temp | Chilled Water | Condenser Water Header | HDR-CWS-RD | Roofdeck/Cooling Tower Area | Main Condenser Water Supply Header Temperature | AI | Temperature Sensor (immersion) | BMS Contractor | BMS-03/Cooling Tower P&ID/MR-2 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.hdr-cwr-rd.temp | Chilled Water | Condenser Water Header | HDR-CWR-RD | Roofdeck/Cooling Tower Area | Main Condenser Water Return Header Temperature | AI | Temperature Sensor (immersion) | BMS Contractor | BMS-03/Cooling Tower P&ID/MR-3 | PNL-CT-RD | BMS-02:r1c2; MC-ME:Cooling Tower
chws.hdr-chws-l2.temp | Chilled Water | CHW Supply Main Header | HDR-CHWS | 2F/CHW Pump Room | CHW Supply Main Header Temperature | AI | Temperature Sensor (immersion) | BMS Contractor | BMS-03/Primary CHW & CW P&ID — header | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:CHW Supply Header
chws.hdr-chws-l2.press | Chilled Water | CHW Supply Main Header | HDR-CHWS | 2F/CHW Pump Room | CHW Supply Main Header Pressure | AI | Pressure Sensor | BMS Contractor | BMS-03/Primary CHW & CW P&ID — header | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:CHW Supply Header
chws.hdr-chwr-l2.temp | Chilled Water | CHW Return Main Header | HDR-CHWR | 2F/CHW Pump Room | CHW Return Main Header Temperature | AI | Temperature Sensor (immersion) | BMS Contractor | BMS-03/Primary CHW & CW P&ID — header | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:CHW Return Header
chws.hdr-chwr-l2.press | Chilled Water | CHW Return Main Header | HDR-CHWR | 2F/CHW Pump Room | CHW Return Main Header Pressure | AI | Pressure Sensor | BMS Contractor | BMS-03/Primary CHW & CW P&ID — header | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:CHW Return Header
chws.hdr-chw-bp.diff-press | Chilled Water | CHW Bypass Header | HDR-CHW-BP | 2F/CHW Pump Room | CHW Differential Pressure (Supply vs. Return) | AI | Differential Pressure Sensor | BMS Contractor | BMS-03/Primary CHW & CW P&ID — bypass | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:CHW Main Header | Drives PCHWP VFD speed control
chws.hdr-chw-bp.diff-temp | Chilled Water | CHW Bypass Header | HDR-CHW-BP | 2F/CHW Pump Room | CHW Differential Temperature (Supply vs. Return) | AI | Differential Temp Sensor | BMS Contractor | BMS-03/Primary CHW & CW P&ID — bypass | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:CHW Main Header
chws.hdr-chw-bp.iso-vlv-stat | Chilled Water | CHW Bypass Header | HDR-CHW-BP | 2F/CHW Pump Room | Isolation Motorized Valve Status — CHW Bypass | DI | Electric Valve Actuator | BMS Contractor | BMS-03/Primary CHW & CW P&ID — bypass | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:CHW Main Header | BMS-supplied actuator on bypass
chws.hdr-chw-bp.iso-vlv-cmd | Chilled Water | CHW Bypass Header | HDR-CHW-BP | 2F/CHW Pump Room | Isolation Motorized Valve Control — CHW Bypass | DO | Electric Valve Actuator | BMS Contractor | BMS-03/Primary CHW & CW P&ID — bypass | PNL-CHWP-L2 | BMS-01:r1c1; MC-ME:CHW Main Header
chws.btu-chws-main.network | Chilled Water | BTU Meter | BTU-CHWS-MAIN | 2F/CHW Pump Room | BTU Meter Modbus Network connection | Network | BTU Meter (Modbus RTU/IP) | BMS Contractor | BMS-03/Primary CHW & CW P&ID — BTU meter | PNL-CHWP-L2 | BMS-03:r0c0/r0c1; MC-ME:Chiller (CHW flow) | Plant-level kWh + Btu energy submetering
chws.btu-chws-main.energy | Chilled Water | BTU Meter | BTU-CHWS-MAIN | 2F/CHW Pump Room | Cumulative thermal energy (kBtu) | HLI | - | BMS Contractor | BMS-03/Primary CHW & CW P&ID — BTU meter | PNL-CHWP-L2 | BMS-03:r0c0/r0c1; MC-ME:Chiller (CHW flow)
chws.btu-chws-main.flow | Chilled Water | BTU Meter | BTU-CHWS-MAIN | 2F/CHW Pump Room | CHW Mass Flow | HLI | - | BMS Contractor | BMS-03/Primary CHW & CW P&ID — BTU meter | PNL-CHWP-L2 | BMS-03:r0c0/r0c1; MC-ME:Chiller (CHW flow)
chws.btu-chws-main.dt | Chilled Water | BTU Meter | BTU-CHWS-MAIN | 2F/CHW Pump Room | CHW Supply-Return Delta Temperature | HLI | - | BMS Contractor | BMS-03/Primary CHW & CW P&ID — BTU meter | PNL-CHWP-L2 | BMS-03:r0c0/r0c1; MC-ME:Chiller (CHW flow)
boh.chwp-1-1.network | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | BACnet/Modbus network to AHU VFD/controller | Network | VFD with BACnet | Equipment Supplier | MC-ME:AHU-AC at 2nd Level/Common Areas; BMS-01 BOH table | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC | 1 network drop per AHU's VFD
boh.chwp-1-1.fan-motor-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC/MR-1 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-1.fan-trip-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC/Alarm-1 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-1.fan-hoa-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-1.vfd-speed-fb | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Variable Frequency Drive (VFD) Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:AHU-AC/MR-7 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC | Via VFD BACnet
boh.chwp-1-1.fan-control-cmd | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Fan Control On/Off/Modulating (speed command) | HLI | VFD | Equipment Supplier | MC-ME:AHU-AC/Turn ON/OFF | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC | Via VFD BACnet
boh.chwp-1-1.supply-air-temp | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Supply Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-6 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-1.mixed-air-temp | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Mixed Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-5 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-1.supply-air-rh | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Supply Air Humidity Monitoring | AI | Humidity Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-1.return-air-temp | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Indoor Return Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-3 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-1.return-air-co2 | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Indoor Return Air CO2 Level | AI | CO2 Sensor (duct) | BMS Contractor | MC-ME:AHU-AC/MR-4 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC | Drives DCV (demand-controlled ventilation)
boh.chwp-1-1.chw-vlv-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Two-Way CHW Modulating Valve Status | DI | Electric Valve Actuator (limit/feedback switch) | ME Contractor | MC-ME:AHU-AC | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC | Valve supplied by ME
boh.chwp-1-1.chw-vlv-cmd | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | CHW Modulating Valve Control On/Off/Modulating | AO | Electric Valve Actuator (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Modulate-1 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC | Drives valve to maintain supply air temp
boh.chwp-1-1.oa-damper-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Outdoor Air Motorized Damper Status | DI | Damper Controller (limit/feedback switch) | ME Contractor | MC-ME:AHU-AC/MR-9 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC | Damper supplied by ME
boh.chwp-1-1.oa-damper-cmd | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Outdoor Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Turn ON/OFF/Modulate | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-1.ra-damper-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Return Air Motorized Damper Status | DI | Damper Controller (limit/feedback switch) | ME Contractor | MC-ME:AHU-AC/MR-8 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-1.ra-damper-cmd | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.1 | GND/BOH AHU Area | Return Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Turn ON/OFF/Modulate | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.network | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | BACnet/Modbus network to AHU VFD/controller | Network | VFD with BACnet | Equipment Supplier | MC-ME:AHU-AC at 2nd Level/Common Areas; BMS-01 BOH table | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.fan-motor-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC/MR-1 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.fan-trip-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC/Alarm-1 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.fan-hoa-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.vfd-speed-fb | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Variable Frequency Drive (VFD) Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:AHU-AC/MR-7 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC | Via VFD BACnet
boh.chwp-1-2.fan-control-cmd | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Fan Control On/Off/Modulating (speed command) | HLI | VFD | Equipment Supplier | MC-ME:AHU-AC/Turn ON/OFF | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC | Via VFD BACnet
boh.chwp-1-2.supply-air-temp | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Supply Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-6 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.mixed-air-temp | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Mixed Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-5 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.supply-air-rh | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Supply Air Humidity Monitoring | AI | Humidity Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.return-air-temp | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Indoor Return Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-3 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.return-air-co2 | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Indoor Return Air CO2 Level | AI | CO2 Sensor (duct) | BMS Contractor | MC-ME:AHU-AC/MR-4 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.chw-vlv-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Two-Way CHW Modulating Valve Status | DI | Electric Valve Actuator (limit/feedback switch) | ME Contractor | MC-ME:AHU-AC | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.chw-vlv-cmd | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | CHW Modulating Valve Control On/Off/Modulating | AO | Electric Valve Actuator (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Modulate-1 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.oa-damper-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Outdoor Air Motorized Damper Status | DI | Damper Controller (limit/feedback switch) | ME Contractor | MC-ME:AHU-AC/MR-9 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.oa-damper-cmd | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Outdoor Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Turn ON/OFF/Modulate | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.ra-damper-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Return Air Motorized Damper Status | DI | Damper Controller (limit/feedback switch) | ME Contractor | MC-ME:AHU-AC/MR-8 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-2.ra-damper-cmd | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.2 | GND/BOH AHU Area | Return Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Turn ON/OFF/Modulate | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.network | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | BACnet/Modbus network to AHU VFD/controller | Network | VFD with BACnet | Equipment Supplier | MC-ME:AHU-AC at 2nd Level/Common Areas; BMS-01 BOH table | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.fan-motor-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC/MR-1 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.fan-trip-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC/Alarm-1 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.fan-hoa-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.vfd-speed-fb | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Variable Frequency Drive (VFD) Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:AHU-AC/MR-7 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC | Via VFD BACnet
boh.chwp-1-3.fan-control-cmd | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Fan Control On/Off/Modulating (speed command) | HLI | VFD | Equipment Supplier | MC-ME:AHU-AC/Turn ON/OFF | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC | Via VFD BACnet
boh.chwp-1-3.supply-air-temp | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Supply Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-6 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.mixed-air-temp | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Mixed Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-5 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.supply-air-rh | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Supply Air Humidity Monitoring | AI | Humidity Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.return-air-temp | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Indoor Return Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-3 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.return-air-co2 | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Indoor Return Air CO2 Level | AI | CO2 Sensor (duct) | BMS Contractor | MC-ME:AHU-AC/MR-4 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.chw-vlv-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Two-Way CHW Modulating Valve Status | DI | Electric Valve Actuator (limit/feedback switch) | ME Contractor | MC-ME:AHU-AC | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.chw-vlv-cmd | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | CHW Modulating Valve Control On/Off/Modulating | AO | Electric Valve Actuator (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Modulate-1 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.oa-damper-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Outdoor Air Motorized Damper Status | DI | Damper Controller (limit/feedback switch) | ME Contractor | MC-ME:AHU-AC/MR-9 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.oa-damper-cmd | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Outdoor Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Turn ON/OFF/Modulate | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.ra-damper-status | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Return Air Motorized Damper Status | DI | Damper Controller (limit/feedback switch) | ME Contractor | MC-ME:AHU-AC/MR-8 | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
boh.chwp-1-3.ra-damper-cmd | BOH Air Handling | AHU (Chilled-Water-Served) | CHWP-1.3 | GND/BOH AHU Area | Return Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Turn ON/OFF/Modulate | PNL-CHWP-GND | BMS-01:r0c1; MC-ME:AHU-AC
pl.hwt-lz-1.tank-temp | Plumbing & Sanitary Hotwater | Calorifier (Hot Water Storage Tank) | HWT-LZ-1 | Lower Ground/HW Plant | Tank Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-PL:Calorifiers/MR-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Calorifiers
pl.hwt-lz-2.tank-temp | Plumbing & Sanitary Hotwater | Calorifier (Hot Water Storage Tank) | HWT-LZ-2 | Lower Ground/HW Plant | Tank Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-PL:Calorifiers/MR-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Calorifiers
pl.hwt-lz-3.tank-temp | Plumbing & Sanitary Hotwater | Calorifier (Hot Water Storage Tank) | HWT-LZ-3 | Lower Ground/HW Plant | Tank Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-PL:Calorifiers/MR-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Calorifiers
pl.hwt-hz-1.tank-temp | Plumbing & Sanitary Hotwater | Calorifier (Hot Water Storage Tank) | HWT-HZ-1 | Roofdeck/HW Plant | Tank Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-PL:Calorifiers/MR-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Calorifiers
pl.hwt-hz-2.tank-temp | Plumbing & Sanitary Hotwater | Calorifier (Hot Water Storage Tank) | HWT-HZ-2 | Roofdeck/HW Plant | Tank Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-PL:Calorifiers/MR-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Calorifiers
pl.hwt-hz-3.tank-temp | Plumbing & Sanitary Hotwater | Calorifier (Hot Water Storage Tank) | HWT-HZ-3 | Roofdeck/HW Plant | Tank Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-PL:Calorifiers/MR-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Calorifiers
pl.hdr-hw-lz.supply-temp | Plumbing & Sanitary Hotwater | Hot Water Header Set | HDR-HW-LZ | Lower Ground/HW Plant | Hot Water Supply Header Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-PL:Supply & Return Headers/MR-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Supply&Return Headers
pl.hdr-hw-lz.return-temp | Plumbing & Sanitary Hotwater | Hot Water Header Set | HDR-HW-LZ | Lower Ground/HW Plant | Hot Water Return Header Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-PL:Supply & Return Headers/MR-3 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Supply&Return Headers
pl.hdr-hw-lz.makeup-temp | Plumbing & Sanitary Hotwater | Hot Water Header Set | HDR-HW-LZ | Lower Ground/HW Plant | Make Up Cold Water Header Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-PL:Supply & Return Headers/MR-2 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Supply&Return Headers
pl.hdr-hw-hz.supply-temp | Plumbing & Sanitary Hotwater | Hot Water Header Set | HDR-HW-HZ | Roofdeck/HW Plant | Hot Water Supply Header Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-PL:Supply & Return Headers/MR-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Supply&Return Headers
pl.hdr-hw-hz.return-temp | Plumbing & Sanitary Hotwater | Hot Water Header Set | HDR-HW-HZ | Roofdeck/HW Plant | Hot Water Return Header Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-PL:Supply & Return Headers/MR-3 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Supply&Return Headers
pl.hdr-hw-hz.makeup-temp | Plumbing & Sanitary Hotwater | Hot Water Header Set | HDR-HW-HZ | Roofdeck/HW Plant | Make Up Cold Water Header Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-PL:Supply & Return Headers/MR-2 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Supply&Return Headers
pl.hp-lz-1.motor-status | Plumbing & Sanitary Hotwater | Heat Pump | HP-LZ-1 | Lower Ground/HW Plant | Pump Motor Status (Run feedback) | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Heat Pump/MR-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001 | Hardwired DI per A-PL-001
pl.hp-lz-1.hoa-status | Plumbing & Sanitary Hotwater | Heat Pump | HP-LZ-1 | Lower Ground/HW Plant | Pump Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Heat Pump/MR-2 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-lz-1.trip-alarm | Plumbing & Sanitary Hotwater | Heat Pump | HP-LZ-1 | Lower Ground/HW Plant | Pump Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Heat Pump/Alarm-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-lz-2.motor-status | Plumbing & Sanitary Hotwater | Heat Pump | HP-LZ-2 | Lower Ground/HW Plant | Pump Motor Status (Run feedback) | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Heat Pump/MR-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-lz-2.hoa-status | Plumbing & Sanitary Hotwater | Heat Pump | HP-LZ-2 | Lower Ground/HW Plant | Pump Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Heat Pump/MR-2 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-lz-2.trip-alarm | Plumbing & Sanitary Hotwater | Heat Pump | HP-LZ-2 | Lower Ground/HW Plant | Pump Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Heat Pump/Alarm-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-lz-3.motor-status | Plumbing & Sanitary Hotwater | Heat Pump | HP-LZ-3 | Lower Ground/HW Plant | Pump Motor Status (Run feedback) | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Heat Pump/MR-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-lz-3.hoa-status | Plumbing & Sanitary Hotwater | Heat Pump | HP-LZ-3 | Lower Ground/HW Plant | Pump Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Heat Pump/MR-2 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-lz-3.trip-alarm | Plumbing & Sanitary Hotwater | Heat Pump | HP-LZ-3 | Lower Ground/HW Plant | Pump Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Heat Pump/Alarm-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.rp-lz-1.motor-status | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-LZ-1 | Lower Ground/HW Plant | Pump Motor Status (Run feedback) | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Circulating Pumps/MR-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-lz-1.hoa-status | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-LZ-1 | Lower Ground/HW Plant | Pump Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Circulating Pumps/MR-2 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-lz-1.trip-alarm | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-LZ-1 | Lower Ground/HW Plant | Pump Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Circulating Pumps/Alarm-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-lz-2.motor-status | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-LZ-2 | Lower Ground/HW Plant | Pump Motor Status (Run feedback) | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Circulating Pumps/MR-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-lz-2.hoa-status | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-LZ-2 | Lower Ground/HW Plant | Pump Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Circulating Pumps/MR-2 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-lz-2.trip-alarm | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-LZ-2 | Lower Ground/HW Plant | Pump Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Circulating Pumps/Alarm-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-lz-3.motor-status | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-LZ-3 | Lower Ground/HW Plant | Pump Motor Status (Run feedback) | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Circulating Pumps/MR-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-lz-3.hoa-status | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-LZ-3 | Lower Ground/HW Plant | Pump Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Circulating Pumps/MR-2 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-lz-3.trip-alarm | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-LZ-3 | Lower Ground/HW Plant | Pump Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-PL:Circulating Pumps/Alarm-1 | PNL-PL-LZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.hp-hz-1.motor-status | Plumbing & Sanitary Hotwater | Heat Pump | HP-HZ-1 | Roofdeck/HW Plant | Pump Motor Status (Run feedback) | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Heat Pump/MR-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001 | Via HZ equipment-panel HLI per A-PL-001
pl.hp-hz-1.hoa-status | Plumbing & Sanitary Hotwater | Heat Pump | HP-HZ-1 | Roofdeck/HW Plant | Pump Motor Hand/Off/Auto Status | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Heat Pump/MR-2 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-hz-1.trip-alarm | Plumbing & Sanitary Hotwater | Heat Pump | HP-HZ-1 | Roofdeck/HW Plant | Pump Trip Alarm Status | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Heat Pump/Alarm-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-hz-2.motor-status | Plumbing & Sanitary Hotwater | Heat Pump | HP-HZ-2 | Roofdeck/HW Plant | Pump Motor Status (Run feedback) | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Heat Pump/MR-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-hz-2.hoa-status | Plumbing & Sanitary Hotwater | Heat Pump | HP-HZ-2 | Roofdeck/HW Plant | Pump Motor Hand/Off/Auto Status | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Heat Pump/MR-2 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-hz-2.trip-alarm | Plumbing & Sanitary Hotwater | Heat Pump | HP-HZ-2 | Roofdeck/HW Plant | Pump Trip Alarm Status | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Heat Pump/Alarm-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-hz-3.motor-status | Plumbing & Sanitary Hotwater | Heat Pump | HP-HZ-3 | Roofdeck/HW Plant | Pump Motor Status (Run feedback) | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Heat Pump/MR-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-hz-3.hoa-status | Plumbing & Sanitary Hotwater | Heat Pump | HP-HZ-3 | Roofdeck/HW Plant | Pump Motor Hand/Off/Auto Status | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Heat Pump/MR-2 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.hp-hz-3.trip-alarm | Plumbing & Sanitary Hotwater | Heat Pump | HP-HZ-3 | Roofdeck/HW Plant | Pump Trip Alarm Status | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Heat Pump/Alarm-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Heat Pump; A-PL-001
pl.rp-hz-1.motor-status | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-HZ-1 | Roofdeck/HW Plant | Pump Motor Status (Run feedback) | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Circulating Pumps/MR-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-hz-1.hoa-status | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-HZ-1 | Roofdeck/HW Plant | Pump Motor Hand/Off/Auto Status | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Circulating Pumps/MR-2 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-hz-1.trip-alarm | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-HZ-1 | Roofdeck/HW Plant | Pump Trip Alarm Status | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Circulating Pumps/Alarm-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-hz-2.motor-status | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-HZ-2 | Roofdeck/HW Plant | Pump Motor Status (Run feedback) | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Circulating Pumps/MR-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-hz-2.hoa-status | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-HZ-2 | Roofdeck/HW Plant | Pump Motor Hand/Off/Auto Status | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Circulating Pumps/MR-2 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-hz-2.trip-alarm | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-HZ-2 | Roofdeck/HW Plant | Pump Trip Alarm Status | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Circulating Pumps/Alarm-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-hz-3.motor-status | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-HZ-3 | Roofdeck/HW Plant | Pump Motor Status (Run feedback) | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Circulating Pumps/MR-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-hz-3.hoa-status | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-HZ-3 | Roofdeck/HW Plant | Pump Motor Hand/Off/Auto Status | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Circulating Pumps/MR-2 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
pl.rp-hz-3.trip-alarm | Plumbing & Sanitary Hotwater | Recirculating Pump | RP-HZ-3 | Roofdeck/HW Plant | Pump Trip Alarm Status | HLI | Auxiliary Contact (via equipment-panel gateway) | Equipment Supplier | MC-PL:Circulating Pumps/Alarm-1 | PNL-PL-HZ | BMS-01:r0c2; MC-PL:Circulating Pumps; A-PL-001
vent.tef-1-1.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-1.1 | GF Main Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.tef-1-1.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-1.1 | GF Main Lobby | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.tef-1-1.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-1.1 | GF Main Lobby | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.tef-1-2.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-1.2 | GF Main Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.tef-1-2.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-1.2 | GF Main Lobby | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.tef-1-2.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-1.2 | GF Main Lobby | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.tef-1-3.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-1.3 | GF Main Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.tef-1-3.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-1.3 | GF Main Lobby | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.tef-1-3.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-1.3 | GF Main Lobby | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.tef-1-4.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-1.4 | GF Main Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.tef-1-4.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-1.4 | GF Main Lobby | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.tef-1-4.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-1.4 | GF Main Lobby | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.ef-1-2a.motor-status | General Ventilation | Exhaust Fan (General) | EF-1.2A | GF Main Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.ef-1-2a.hoa-status | General Ventilation | Exhaust Fan (General) | EF-1.2A | GF Main Lobby | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.ef-1-2a.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-1.2A | GF Main Lobby | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.ef-lpg-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-LPG.1 | GF Main Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS | LPG room exhaust
vent.ef-lpg-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-LPG.1 | GF Main Lobby | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.ef-lpg-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-LPG.1 | GF Main Lobby | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.ef-1mr-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-1MR.1 | GF Main Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS | Mechanical room exhaust
vent.ef-1mr-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-1MR.1 | GF Main Lobby | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.ef-1mr-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-1MR.1 | GF Main Lobby | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.ef-1st0-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-1ST0.1 | GF Main Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS | Storage room exhaust
vent.ef-1st0-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-1ST0.1 | GF Main Lobby | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.ef-1st0-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-1ST0.1 | GF Main Lobby | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.ef-mrf-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-MRF.1 | GF Main Lobby | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.ef-mrf-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-MRF.1 | GF Main Lobby | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.ef-mrf-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-MRF.1 | GF Main Lobby | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-GF | BMS-01:r0c2; MC-ME:EAS
vent.tef-2-1.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-2.1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.tef-2-1.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-2.1 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.tef-2-1.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-2.1 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.tef-2-3.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-2.3 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.tef-2-3.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-2.3 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.tef-2-3.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-2.3 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.tef-2b-3.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-2B.3 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.tef-2b-3.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-2B.3 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.tef-2b-3.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-2B.3 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2b-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-2B.1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2b-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-2B.1 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2b-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-2B.1 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2b-2.motor-status | General Ventilation | Exhaust Fan (General) | EF-2B.2 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2b-2.hoa-status | General Ventilation | Exhaust Fan (General) | EF-2B.2 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2b-2.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-2B.2 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-gs-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-GS.1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-gs-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-GS.1 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-gs-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-GS.1 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-gs-2.motor-status | General Ventilation | Exhaust Fan (General) | EF-GS.2 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-gs-2.hoa-status | General Ventilation | Exhaust Fan (General) | EF-GS.2 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-gs-2.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-GS.2 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-2.1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-2.1 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-2.1 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2-2.motor-status | General Ventilation | Exhaust Fan (General) | EF-2.2 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2-2.hoa-status | General Ventilation | Exhaust Fan (General) | EF-2.2 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2-2.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-2.2 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2-3.motor-status | General Ventilation | Exhaust Fan (General) | EF-2.3 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2-3.hoa-status | General Ventilation | Exhaust Fan (General) | EF-2.3 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2-3.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-2.3 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2-4.motor-status | General Ventilation | Exhaust Fan (General) | EF-2.4 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2-4.hoa-status | General Ventilation | Exhaust Fan (General) | EF-2.4 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-2-4.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-2.4 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-chr-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-CHR.1 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS | Chiller room exhaust
vent.ef-chr-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-CHR.1 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-chr-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-CHR.1 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-chr-2.motor-status | General Ventilation | Exhaust Fan (General) | EF-CHR.2 | 2nd Floor | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-chr-2.hoa-status | General Ventilation | Exhaust Fan (General) | EF-CHR.2 | 2nd Floor | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.ef-chr-2.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-CHR.2 | 2nd Floor | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L2 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3a-1.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3A.1 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3a-1.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3A.1 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3a-1.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3A.1 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3a-2.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3A.2 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3a-2.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3A.2 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3a-2.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3A.2 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3b.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3B | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3b.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3B | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3b.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3B | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3c-1.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3C.1 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3c-1.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3C.1 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3c-1.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3C.1 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3c-2.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3C.2 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3c-2.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3C.2 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3c-2.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3C.2 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-01.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.1 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-01.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.1 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-01.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.1 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-02.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.2 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-02.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.2 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-02.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.2 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-03.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.3 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-03.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.3 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-03.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.3 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-04.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.4 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-04.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.4 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-04.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.4 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-05.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.5 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-05.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.5 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-05.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.5 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-06.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.6 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-06.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.6 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-06.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.6 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-07.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.7 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-07.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.7 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-07.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.7 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-08.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.8 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-08.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.8 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-08.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.8 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-09.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.9 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-09.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.9 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-09.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.9 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-10.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.10 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-10.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.10 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-10.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.10 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-11.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.11 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-11.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.11 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-11.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.11 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-12.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.12 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-12.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.12 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-12.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.12 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-13.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.13 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-13.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.13 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-13.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.13 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-14.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.14 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-14.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.14 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-14.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.14 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-15.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.15 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-15.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.15 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-15.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.15 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-16.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.16 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-16.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.16 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-16.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.16 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-17.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.17 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-17.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.17 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-17.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.17 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-18.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.18 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-18.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.18 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-18.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.18 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-19.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.19 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-19.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.19 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-19.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.19 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-20.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.20 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-20.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.20 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.tef-3d-20.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-3D.20 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r0c2; MC-ME:EAS
vent.ef-3-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-3.1 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r1c2; MC-ME:EAS
vent.ef-3-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-3.1 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r1c2; MC-ME:EAS
vent.ef-3-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-3.1 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r1c2; MC-ME:EAS
vent.ef-3-2.motor-status | General Ventilation | Exhaust Fan (General) | EF-3.2 | 3rd Amenity & Guestroom | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-L3 | BMS-01:r1c2; MC-ME:EAS
vent.ef-3-2.hoa-status | General Ventilation | Exhaust Fan (General) | EF-3.2 | 3rd Amenity & Guestroom | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-L3 | BMS-01:r1c2; MC-ME:EAS
vent.ef-3-2.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-3.2 | 3rd Amenity & Guestroom | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-L3 | BMS-01:r1c2; MC-ME:EAS
vent.tef-b-1.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-B.1 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.tef-b-1.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-B.1 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.tef-b-1.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-B.1 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.tef-b-2.motor-status | General Ventilation | Exhaust Fan (Toilet) | TEF-B.2 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.tef-b-2.hoa-status | General Ventilation | Exhaust Fan (Toilet) | TEF-B.2 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.tef-b-2.trip-alarm | General Ventilation | Exhaust Fan (Toilet) | TEF-B.2 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-b-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-B.1 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-b-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-B.1 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-b-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-B.1 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-b-2.motor-status | General Ventilation | Exhaust Fan (General) | EF-B.2 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-b-2.hoa-status | General Ventilation | Exhaust Fan (General) | EF-B.2 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-b-2.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-B.2 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-bs-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-BS.1 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-bs-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-BS.1 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-bs-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-BS.1 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-bs-2.motor-status | General Ventilation | Exhaust Fan (General) | EF-BS.2 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-bs-2.hoa-status | General Ventilation | Exhaust Fan (General) | EF-BS.2 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-bs-2.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-BS.2 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-glz-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-GLZ.1 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-glz-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-GLZ.1 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-glz-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-GLZ.1 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-glz-2.motor-status | General Ventilation | Exhaust Fan (General) | EF-GLZ.2 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-glz-2.hoa-status | General Ventilation | Exhaust Fan (General) | EF-GLZ.2 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-glz-2.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-GLZ.2 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-3sf-2.motor-status | General Ventilation | Exhaust Fan (General) | EF-3SF.2 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-3sf-2.hoa-status | General Ventilation | Exhaust Fan (General) | EF-3SF.2 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-3sf-2.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-3SF.2 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-8r-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-8R.1 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS | Tag as-read; verify Q-008
vent.ef-8r-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-8R.1 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-8r-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-8R.1 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-rr-2.motor-status | General Ventilation | Exhaust Fan (General) | EF-RR.2 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS | Tag as-read; verify Q-008
vent.ef-rr-2.hoa-status | General Ventilation | Exhaust Fan (General) | EF-RR.2 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-rr-2.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-RR.2 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-mc-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-MC.1 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-mc-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-MC.1 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-mc-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-MC.1 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-hp-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-HP.1 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-hp-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-HP.1 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-hp-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-HP.1 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-pr-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-PR.1 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-pr-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-PR.1 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-pr-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-PR.1 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-mfp-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-MFP.1 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-mfp-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-MFP.1 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-mfp-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-MFP.1 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-pr-2.motor-status | General Ventilation | Exhaust Fan (General) | EF-PR.2 | Basement | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-pr-2.hoa-status | General Ventilation | Exhaust Fan (General) | EF-PR.2 | Basement | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-pr-2.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-PR.2 | Basement | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-BSMT | BMS-01:r1c2; MC-ME:EAS
vent.ef-rd-1.motor-status | General Ventilation | Exhaust Fan (General) | EF-RD.1 | Roofdeck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-RD | BMS-01:r1c2; MC-ME:EAS
vent.ef-rd-1.hoa-status | General Ventilation | Exhaust Fan (General) | EF-RD.1 | Roofdeck | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-RD | BMS-01:r1c2; MC-ME:EAS
vent.ef-rd-1.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-RD.1 | Roofdeck | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-RD | BMS-01:r1c2; MC-ME:EAS
vent.ef-rd-2.motor-status | General Ventilation | Exhaust Fan (General) | EF-RD.2 | Roofdeck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-RD | BMS-01:r1c2; MC-ME:EAS
vent.ef-rd-2.hoa-status | General Ventilation | Exhaust Fan (General) | EF-RD.2 | Roofdeck | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-RD | BMS-01:r1c2; MC-ME:EAS
vent.ef-rd-2.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-RD.2 | Roofdeck | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-RD | BMS-01:r1c2; MC-ME:EAS
vent.ef-rd-extra.motor-status | General Ventilation | Exhaust Fan (General) | EF-1 (RD) | Roofdeck | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-1 | PNL-VENT-RD | BMS-01:r1c2; MC-ME:EAS | Tag '(EF-1)' as-read; refine if Q-008 reveals different tag
vent.ef-rd-extra.hoa-status | General Ventilation | Exhaust Fan (General) | EF-1 (RD) | Roofdeck | Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/MR-2 | PNL-VENT-RD | BMS-01:r1c2; MC-ME:EAS
vent.ef-rd-extra.trip-alarm | General Ventilation | Exhaust Fan (General) | EF-1 (RD) | Roofdeck | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:EAS/Alarm-1 | PNL-VENT-RD | BMS-01:r1c2; MC-ME:EAS
bl.sb-1.steam-pressure | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Supply Steam Pressure | AI | Pressure Sensor | BMS Contractor | MC-ME:Boiler/MR-11 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.feedwater-temp | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Feedwater Supply Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-ME:Boiler | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.fluegas-temp | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Fluegas Temperature | AI | Temperature Sensor (high-temp/duct insertion) | BMS Contractor | MC-ME:Boiler/MR-8 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.fluegas-o2 | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Fluegas Oxygen Level | AI | Oxygen Sensor | BMS Contractor | MC-ME:Boiler/MR-9 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.water-level-low | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Low Water Level | DI | Level Sensor | Equipment Supplier | MC-ME:Boiler/Alarm-3 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.water-level-high | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | High Water Level | DI | Level Sensor | Equipment Supplier | MC-ME:Boiler/Alarm-3 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.burner-power | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Burner Power | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.fire-small | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Small Fire Control Signal | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler/MR-5 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.fire-big | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Big Fire Control Signal | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler/MR-6 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.waterfeed-pump | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Waterfeed Pump Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler/MR-4 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.burner-status | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Burner Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler/MR-2 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.burner-running | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Burner Fire Running Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.blower-status | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Blower Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler/MR-3 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.fuel-oil-pump | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Fuel Oil Pump Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler/MR-1 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-1.blowdown-vlv-stat | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Motorized Valve Status — Blowdown Water | DI | Electric Valve Actuator (limit switch) | BMS Contractor | MC-ME:Boiler/MR-7 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler | BMS-supplied actuator
bl.sb-1.blowdown-vlv-cmd | Boiler/Laundry | Steam Boiler | SB-1 | Lower Ground/Boiler Room | Motorized Valve Control — Blowdown Water | DO | Electric Valve Actuator | BMS Contractor | MC-ME:Boiler/Turn ON/OFF blowdown | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.steam-pressure | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Supply Steam Pressure | AI | Pressure Sensor | BMS Contractor | MC-ME:Boiler/MR-11 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.feedwater-temp | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Feedwater Supply Temperature | AI | Temperature Sensor (immersion/thermowell) | BMS Contractor | MC-ME:Boiler | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.fluegas-temp | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Fluegas Temperature | AI | Temperature Sensor (high-temp/duct insertion) | BMS Contractor | MC-ME:Boiler/MR-8 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.fluegas-o2 | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Fluegas Oxygen Level | AI | Oxygen Sensor | BMS Contractor | MC-ME:Boiler/MR-9 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.water-level-low | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Low Water Level | DI | Level Sensor | Equipment Supplier | MC-ME:Boiler/Alarm-3 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.water-level-high | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | High Water Level | DI | Level Sensor | Equipment Supplier | MC-ME:Boiler/Alarm-3 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.burner-power | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Burner Power | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.fire-small | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Small Fire Control Signal | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler/MR-5 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.fire-big | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Big Fire Control Signal | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler/MR-6 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.waterfeed-pump | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Waterfeed Pump Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler/MR-4 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.burner-status | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Burner Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler/MR-2 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.burner-running | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Burner Fire Running Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.blower-status | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Blower Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler/MR-3 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.fuel-oil-pump | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Fuel Oil Pump Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:Boiler/MR-1 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.blowdown-vlv-stat | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Motorized Valve Status — Blowdown Water | DI | Electric Valve Actuator (limit switch) | BMS Contractor | MC-ME:Boiler/MR-7 | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
bl.sb-2.blowdown-vlv-cmd | Boiler/Laundry | Steam Boiler | SB-2 | Lower Ground/Boiler Room | Motorized Valve Control — Blowdown Water | DO | Electric Valve Actuator | BMS Contractor | MC-ME:Boiler/Turn ON/OFF blowdown | PNL-BL-LZ | BMS-01:r1c1; MC-ME:Boiler
doas.doas-2w.network | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | BACnet/IP gateway to DOAS controller | Network | DOAS Controller (BACnet) | Equipment Supplier | MC-ME:Common Areas DOAS; BMS-02 Casino MVAC | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.faf-start-cmd | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Fresh Air Fan Start/Stop Control | DO | Contactor relay | Equipment Supplier | MC-ME:DOAS/Turn ON/OFF | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.faf-motor-status | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Fresh Air Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/MR-1 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.faf-hoa-status | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Fresh Air Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/MR-2 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.faf-trip-alarm | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Fresh Air Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/Alarm-1 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.faf-vfd-speed-fb | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Fresh Air Fan VFD Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:DOAS/MR-4 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS | Via VFD BACnet
doas.doas-2w.faf-vfd-control | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Fresh Air Fan Control On/Off/Modulating | HLI | VFD | Equipment Supplier | MC-ME:DOAS/Turn ON/OFF/Modulate | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS | Via VFD BACnet
doas.doas-2w.oa-db-temp | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Outdoor (Ambient) Dry-Bulb Temperature | AI | Temperature Sensor (outdoor/duct) | BMS Contractor | MC-ME:DOAS/MR-7 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.oa-flow | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Outdoor Air Flow Monitoring (Outside-Supply Air) | AI | Flow Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-7 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.oa-rh | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Outdoor Air Humidity Monitoring (Outdoor-Supply Air) | AI | Humidity Sensor (outdoor/duct) | BMS Contractor | MC-ME:DOAS/MR-7 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.oa-damper-status | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Outdoor Air Motorized Damper Status | DI | Damper Controller (limit/feedback) | ME Contractor | MC-ME:DOAS/MR-5 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS | Damper supplied by ME
doas.doas-2w.oa-damper-cmd | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Outdoor Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:DOAS/Turn ON/OFF/Modulate-3 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.mixed-air-temp | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Indoor Mixed Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-8 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.mixed-air-rh | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Indoor Mixed Air Humidity | AI | Humidity Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-9 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.chw-vlv-status | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Two-Way CHW Modulating Valve Status | DI | Electric Valve Actuator (limit switch) | ME Contractor | MC-ME:DOAS/MR-6 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS | Valve supplied by ME
doas.doas-2w.chw-vlv-cmd | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | CHW Modulating Valve Control On/Off/Modulating | AO | Electric Valve Actuator (0-10V/4-20mA) | ME Contractor | MC-ME:DOAS/Modulate-4 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.supply-air-temp | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Indoor Supply Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-10 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.supply-air-rh | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Indoor Supply Air Humidity | AI | Humidity Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.exhaust-air-temp | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Indoor Exhaust Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-11 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.eaf-start-cmd | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Exhaust Fan Start/Stop Control | DO | Contactor relay | Equipment Supplier | MC-ME:DOAS/Turn ON/OFF | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.eaf-motor-status | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Exhaust Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/MR-1 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.eaf-hoa-status | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Exhaust Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/MR-2 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.eaf-trip-alarm | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Exhaust Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/Alarm-1 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.eaf-static-press | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Exhaust Fan Static Pressure Transmitter | AI | Differential Pressure Sensor (duct) | BMS Contractor | MC-ME:DOAS | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS
doas.doas-2w.eaf-vfd-speed-fb | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Exhaust Fan VFD Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:DOAS/MR-4 | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS | Via VFD BACnet
doas.doas-2w.eaf-vfd-control | DOAS - Casino MVAC | DOAS Unit | DOAS-2W | 2nd Level/Casino MVAC Plant | Exhaust Fan Control On/Off/Modulating | HLI | VFD | Equipment Supplier | MC-ME:DOAS/Turn ON/OFF | PNL-DOAS-L2 | BMS-02:r0c1; MC-ME:DOAS | Via VFD BACnet
doas.doas-rd-1.network | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | BACnet/IP gateway to DOAS controller | Network | DOAS Controller (BACnet) | Equipment Supplier | MC-ME:Roof Deck DOAS Serving Guestrooms; BMS-02 Hotel/Roofdeck | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.faf-start-cmd | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Fresh Air Fan Start/Stop Control | DO | Contactor relay | Equipment Supplier | MC-ME:DOAS/Turn ON/OFF | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.faf-motor-status | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Fresh Air Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/MR-1 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.faf-hoa-status | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Fresh Air Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/MR-2 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.faf-trip-alarm | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Fresh Air Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/Alarm-1 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.faf-vfd-speed-fb | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Fresh Air Fan VFD Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:DOAS/MR-4 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.faf-vfd-control | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Fresh Air Fan Control On/Off/Modulating | HLI | VFD | Equipment Supplier | MC-ME:DOAS/Turn ON/OFF/Modulate | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.oa-db-temp | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Outdoor (Ambient) Dry-Bulb Temperature | AI | Temperature Sensor (outdoor/duct) | BMS Contractor | MC-ME:DOAS/MR-7 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.oa-flow | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Outdoor Air Flow Monitoring (Outside-Supply Air) | AI | Flow Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-7 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.oa-rh | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Outdoor Air Humidity Monitoring (Outdoor-Supply Air) | AI | Humidity Sensor (outdoor/duct) | BMS Contractor | MC-ME:DOAS/MR-7 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.oa-damper-status | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Outdoor Air Motorized Damper Status | DI | Damper Controller (limit/feedback) | ME Contractor | MC-ME:DOAS/MR-5 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.oa-damper-cmd | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Outdoor Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:DOAS/Turn ON/OFF/Modulate-3 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.mixed-air-temp | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Indoor Mixed Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-8 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.mixed-air-rh | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Indoor Mixed Air Humidity | AI | Humidity Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-9 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.chw-vlv-status | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Two-Way CHW Modulating Valve Status | DI | Electric Valve Actuator (limit switch) | ME Contractor | MC-ME:DOAS/MR-6 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.chw-vlv-cmd | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | CHW Modulating Valve Control On/Off/Modulating | AO | Electric Valve Actuator (0-10V/4-20mA) | ME Contractor | MC-ME:DOAS/Modulate-4 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.supply-air-temp | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Indoor Supply Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-10 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.exhaust-air-rh | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Indoor Exhaust Air Humidity | AI | Humidity Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS | Roofdeck DOAS uses exhaust RH (not supply) per MC Standards Roof Deck section
doas.doas-rd-1.exhaust-air-temp | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Indoor Exhaust Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-11 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.eaf-start-cmd | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Exhaust Fan Start/Stop Control | DO | Contactor relay | Equipment Supplier | MC-ME:DOAS/Turn ON/OFF | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.eaf-motor-status | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Exhaust Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/MR-1 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.eaf-hoa-status | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Exhaust Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/MR-2 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.eaf-trip-alarm | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Exhaust Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/Alarm-1 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.eaf-static-press | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Exhaust Fan Static Pressure Transmitter | AI | Differential Pressure Sensor (duct) | BMS Contractor | MC-ME:DOAS | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.eaf-vfd-speed-fb | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Exhaust Fan VFD Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:DOAS/MR-4 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-1.eaf-vfd-control | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.1 | Roofdeck/Hotel DOAS Plant | Exhaust Fan Control On/Off/Modulating | HLI | VFD | Equipment Supplier | MC-ME:DOAS/Turn ON/OFF | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.network | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | BACnet/IP gateway to DOAS controller | Network | DOAS Controller (BACnet) | Equipment Supplier | MC-ME:Roof Deck DOAS Serving Guestrooms; BMS-02 Hotel/Roofdeck | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.faf-start-cmd | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Fresh Air Fan Start/Stop Control | DO | Contactor relay | Equipment Supplier | MC-ME:DOAS/Turn ON/OFF | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.faf-motor-status | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Fresh Air Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/MR-1 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.faf-hoa-status | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Fresh Air Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/MR-2 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.faf-trip-alarm | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Fresh Air Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/Alarm-1 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.faf-vfd-speed-fb | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Fresh Air Fan VFD Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:DOAS/MR-4 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.faf-vfd-control | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Fresh Air Fan Control On/Off/Modulating | HLI | VFD | Equipment Supplier | MC-ME:DOAS/Turn ON/OFF/Modulate | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.oa-db-temp | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Outdoor (Ambient) Dry-Bulb Temperature | AI | Temperature Sensor (outdoor/duct) | BMS Contractor | MC-ME:DOAS/MR-7 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.oa-flow | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Outdoor Air Flow Monitoring (Outside-Supply Air) | AI | Flow Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-7 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.oa-rh | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Outdoor Air Humidity Monitoring (Outdoor-Supply Air) | AI | Humidity Sensor (outdoor/duct) | BMS Contractor | MC-ME:DOAS/MR-7 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.oa-damper-status | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Outdoor Air Motorized Damper Status | DI | Damper Controller (limit/feedback) | ME Contractor | MC-ME:DOAS/MR-5 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.oa-damper-cmd | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Outdoor Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:DOAS/Turn ON/OFF/Modulate-3 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.mixed-air-temp | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Indoor Mixed Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-8 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.mixed-air-rh | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Indoor Mixed Air Humidity | AI | Humidity Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-9 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.chw-vlv-status | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Two-Way CHW Modulating Valve Status | DI | Electric Valve Actuator (limit switch) | ME Contractor | MC-ME:DOAS/MR-6 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.chw-vlv-cmd | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | CHW Modulating Valve Control On/Off/Modulating | AO | Electric Valve Actuator (0-10V/4-20mA) | ME Contractor | MC-ME:DOAS/Modulate-4 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.supply-air-temp | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Indoor Supply Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-10 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.exhaust-air-rh | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Indoor Exhaust Air Humidity | AI | Humidity Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.exhaust-air-temp | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Indoor Exhaust Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:DOAS/MR-11 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.eaf-start-cmd | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Exhaust Fan Start/Stop Control | DO | Contactor relay | Equipment Supplier | MC-ME:DOAS/Turn ON/OFF | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.eaf-motor-status | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Exhaust Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/MR-1 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.eaf-hoa-status | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Exhaust Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/MR-2 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.eaf-trip-alarm | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Exhaust Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:DOAS/Alarm-1 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.eaf-static-press | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Exhaust Fan Static Pressure Transmitter | AI | Differential Pressure Sensor (duct) | BMS Contractor | MC-ME:DOAS | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.eaf-vfd-speed-fb | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Exhaust Fan VFD Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:DOAS/MR-4 | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
doas.doas-rd-2.eaf-vfd-control | DOAS - Hotel/Roofdeck | DOAS Unit | DOAS-RD.2 | Roofdeck/Hotel DOAS Plant | Exhaust Fan Control On/Off/Modulating | HLI | VFD | Equipment Supplier | MC-ME:DOAS/Turn ON/OFF | PNL-DOAS-RD | BMS-02:r1c1; MC-ME:DOAS
ahu.ahu-2m-1.network | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | BACnet/IP gateway to AHU controller | Network | AHU Controller (BACnet) | Equipment Supplier | MC-ME:AHU-AC at 2nd Level; BMS-02 AHU 2nd Level | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-1.fan-motor-status | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC/MR-1 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-1.fan-trip-status | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC/Alarm-1 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-1.vfd-speed-fb | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | VFD Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:AHU-AC/MR-7 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC | Via VFD BACnet
ahu.ahu-2m-1.fan-control-cmd | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Fan Control On/Off/Modulating | HLI | VFD | Equipment Supplier | MC-ME:AHU-AC/Turn ON/OFF | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC | Via VFD BACnet
ahu.ahu-2m-1.supply-air-temp | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Supply Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-6 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-1.mixed-air-temp | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Mixed Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-5 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-1.supply-air-rh | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Supply Air Humidity Monitoring | AI | Humidity Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-1.chw-vlv-cmd | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | CHW Modulating Valve Control On/Off/Modulating | AO | Electric Valve Actuator (0-10V/4-20mA) | ME Contractor | MC-ME:AHU-AC/Modulate-1 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC | Modulating valve — feedback via AO command, status implied
ahu.ahu-2m-1.oa-damper-fb | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Outdoor Air Motorized Damper Position Feedback | AI | Damper Controller (0-10V or 4-20mA fb) | ME Contractor | MC-ME:AHU-AC/MR-9 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC | Modulating damper — % position via AI
ahu.ahu-2m-1.oa-damper-cmd | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Outdoor Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Turn ON/OFF/Modulate | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-1.ra-damper-fb | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Return Air Motorized Damper Position Feedback | AI | Damper Controller (0-10V or 4-20mA fb) | ME Contractor | MC-ME:AHU-AC/MR-8 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC | Modulating damper — % position via AI
ahu.ahu-2m-1.ra-damper-cmd | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Return Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Turn ON/OFF/Modulate | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-1.return-air-co2 | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Carbon Dioxide (CO2) Sensor at Return Duct | AI | CO2 Sensor (duct) | BMS Contractor | MC-ME:AHU-AC/MR-4 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-1.return-air-co | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Carbon Monoxide (CO) Sensor at Return Duct | AI | CO Sensor (duct) | BMS Contractor | MC-ME:AHU-AC | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC | Casino-specific (smoking area air quality)
ahu.ahu-2m-1.return-air-temp | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.1 | 2nd Level/Casino MVAC Plant | Indoor Return Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-3 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.network | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | BACnet/IP gateway to AHU controller | Network | AHU Controller (BACnet) | Equipment Supplier | MC-ME:AHU-AC at 2nd Level; BMS-02 AHU 2nd Level | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.fan-motor-status | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC/MR-1 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.fan-trip-status | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:AHU-AC/Alarm-1 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.vfd-speed-fb | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | VFD Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:AHU-AC/MR-7 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.fan-control-cmd | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Fan Control On/Off/Modulating | HLI | VFD | Equipment Supplier | MC-ME:AHU-AC/Turn ON/OFF | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.supply-air-temp | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Supply Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-6 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.mixed-air-temp | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Mixed Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-5 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.supply-air-rh | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Supply Air Humidity Monitoring | AI | Humidity Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.chw-vlv-cmd | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | CHW Modulating Valve Control On/Off/Modulating | AO | Electric Valve Actuator (0-10V/4-20mA) | ME Contractor | MC-ME:AHU-AC/Modulate-1 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.oa-damper-fb | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Outdoor Air Motorized Damper Position Feedback | AI | Damper Controller (0-10V or 4-20mA fb) | ME Contractor | MC-ME:AHU-AC/MR-9 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.oa-damper-cmd | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Outdoor Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Turn ON/OFF/Modulate | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.ra-damper-fb | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Return Air Motorized Damper Position Feedback | AI | Damper Controller (0-10V or 4-20mA fb) | ME Contractor | MC-ME:AHU-AC/MR-8 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.ra-damper-cmd | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Return Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | ME Contractor | MC-ME:AHU-AC/Turn ON/OFF/Modulate | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.return-air-co2 | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Carbon Dioxide (CO2) Sensor at Return Duct | AI | CO2 Sensor (duct) | BMS Contractor | MC-ME:AHU-AC/MR-4 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.return-air-co | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Carbon Monoxide (CO) Sensor at Return Duct | AI | CO Sensor (duct) | BMS Contractor | MC-ME:AHU-AC | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.ahu-2m-2.return-air-temp | AHU - Casino | AHU (Modulating CHW-served) | AHU-2M.2 | 2nd Level/Casino MVAC Plant | Indoor Return Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:AHU-AC/MR-3 | PNL-AHU-L2 | BMS-02:r0c2; MC-ME:AHU-AC
ahu.oz-2m-1.equipment-status | AHU - Casino (Ozonizer) | Ozone Generator (UV-light or Corona) | OZ-2M.1 | 2nd Level/Casino MVAC Plant | Equipment Status | DI | Auxiliary Contact | Equipment Supplier | BMS-02:r0c2 OZONIZERS | PNL-AHU-L2 | BMS-02:r0c2 | Casino air-treatment device paired with AHU-2M.1
ahu.oz-2m-1.equipment-trip | AHU - Casino (Ozonizer) | Ozone Generator (UV-light or Corona) | OZ-2M.1 | 2nd Level/Casino MVAC Plant | Equipment Trip Status | DI | Auxiliary Contact | Equipment Supplier | BMS-02:r0c2 OZONIZERS | PNL-AHU-L2 | BMS-02:r0c2
ahu.oz-2m-1.voc | AHU - Casino (Ozonizer) | Ozone Generator (UV-light or Corona) | OZ-2M.1 | 2nd Level/Casino MVAC Plant | VOC Monitoring (downstream air quality) | AI | VOC Sensor (duct) | BMS Contractor | BMS-02:r0c2 OZONIZERS | PNL-AHU-L2 | BMS-02:r0c2
ahu.oz-2m-2.equipment-status | AHU - Casino (Ozonizer) | Ozone Generator (UV-light or Corona) | OZ-2M.2 | 2nd Level/Casino MVAC Plant | Equipment Status | DI | Auxiliary Contact | Equipment Supplier | BMS-02:r0c2 OZONIZERS | PNL-AHU-L2 | BMS-02:r0c2 | Casino air-treatment device paired with AHU-2M.2
ahu.oz-2m-2.equipment-trip | AHU - Casino (Ozonizer) | Ozone Generator (UV-light or Corona) | OZ-2M.2 | 2nd Level/Casino MVAC Plant | Equipment Trip Status | DI | Auxiliary Contact | Equipment Supplier | BMS-02:r0c2 OZONIZERS | PNL-AHU-L2 | BMS-02:r0c2
ahu.oz-2m-2.voc | AHU - Casino (Ozonizer) | Ozone Generator (UV-light or Corona) | OZ-2M.2 | 2nd Level/Casino MVAC Plant | VOC Monitoring (downstream air quality) | AI | VOC Sensor (duct) | BMS Contractor | BMS-02:r0c2 OZONIZERS | PNL-AHU-L2 | BMS-02:r0c2
pahu.pahu-rd-1.network | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | BACnet/IP gateway to PAHU controller | Network | PAHU Controller (BACnet) | Equipment Supplier | MC-ME:Roof Deck PAHU; BMS-02 PAHU Roofdeck | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.faf-start-cmd | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | Fresh Air Fan Start/Stop Control | DO | Contactor relay | Equipment Supplier | MC-ME:PAHU/Turn ON/OFF | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.faf-motor-status | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | Fresh Air Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:PAHU/MR-1 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.faf-trip | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | Fresh Air Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:PAHU/Alarm-1 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.faf-hoa | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | Fresh Air Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:PAHU/MR-2 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.vfd-speed-fb | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | VFD Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:PAHU/MR-3 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.fan-control-cmd | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | Fan Control On/Off/Modulating | HLI | VFD | Equipment Supplier | MC-ME:PAHU/Turn ON/OFF/Modulate | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.oa-temp | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | Outdoor (Outside) Supply Air Temperature | AI | Temperature Sensor (outdoor/duct) | BMS Contractor | MC-ME:PAHU/MR-6 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.oa-flow | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | Outdoor Air Flow Monitoring | AI | Flow Sensor (duct insertion) | BMS Contractor | MC-ME:PAHU/MR-6 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.supply-temp | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | Indoor Supply Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:PAHU/MR-7 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.faf-static-press | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | Fresh Air Fan Static Pressure Transmitter | AI | Differential Pressure Sensor (duct) | BMS Contractor | MC-ME:PAHU | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.oa-damper-status | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | Outdoor Air Motorized Damper Status | DI | Damper Controller (limit/feedback) | Equipment Supplier | MC-ME:PAHU/MR-4 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.oa-damper-cmd | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | Outdoor Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | Equipment Supplier | MC-ME:PAHU/Turn ON/OFF/Modulate-2 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-1.chw-vlv-cmd | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.1 | Roofdeck/PAHU Plant | CHW Modulating Valve Control On/Off/Modulating | AO | Electric Valve Actuator (0-10V/4-20mA) | ME Contractor | MC-ME:PAHU/Modulate-3 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.network | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | BACnet/IP gateway to PAHU controller | Network | PAHU Controller (BACnet) | Equipment Supplier | MC-ME:Roof Deck PAHU; BMS-02 PAHU Roofdeck | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.faf-start-cmd | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | Fresh Air Fan Start/Stop Control | DO | Contactor relay | Equipment Supplier | MC-ME:PAHU/Turn ON/OFF | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.faf-motor-status | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | Fresh Air Fan Motor Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:PAHU/MR-1 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.faf-trip | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | Fresh Air Fan Trip Alarm Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:PAHU/Alarm-1 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.faf-hoa | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | Fresh Air Fan Motor Hand/Off/Auto Status | DI | Auxiliary Contact | Equipment Supplier | MC-ME:PAHU/MR-2 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.vfd-speed-fb | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | VFD Speed Monitoring (feedback) | HLI | VFD | Equipment Supplier | MC-ME:PAHU/MR-3 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.fan-control-cmd | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | Fan Control On/Off/Modulating | HLI | VFD | Equipment Supplier | MC-ME:PAHU/Turn ON/OFF/Modulate | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.oa-temp | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | Outdoor (Outside) Supply Air Temperature | AI | Temperature Sensor (outdoor/duct) | BMS Contractor | MC-ME:PAHU/MR-6 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.oa-flow | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | Outdoor Air Flow Monitoring | AI | Flow Sensor (duct insertion) | BMS Contractor | MC-ME:PAHU/MR-6 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.supply-temp | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | Indoor Supply Air Temperature | AI | Temperature Sensor (duct insertion) | BMS Contractor | MC-ME:PAHU/MR-7 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.faf-static-press | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | Fresh Air Fan Static Pressure Transmitter | AI | Differential Pressure Sensor (duct) | BMS Contractor | MC-ME:PAHU | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.oa-damper-status | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | Outdoor Air Motorized Damper Status | DI | Damper Controller (limit/feedback) | Equipment Supplier | MC-ME:PAHU/MR-4 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.oa-damper-cmd | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | Outdoor Air Motorized Damper Control On/Off/Modulating | AO | Damper Controller (0-10V or 4-20mA) | Equipment Supplier | MC-ME:PAHU/Turn ON/OFF/Modulate-2 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
pahu.pahu-rd-2.chw-vlv-cmd | PAHU - Roofdeck | Precooled Air Handling Unit | PAHU-RD.2 | Roofdeck/PAHU Plant | CHW Modulating Valve Control On/Off/Modulating | AO | Electric Valve Actuator (0-10V/4-20mA) | ME Contractor | MC-ME:PAHU/Modulate-3 | PNL-PAHU-RD | BMS-02:r0c2; MC-ME:PAHU
ee.mtr-main-1.network | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-1 | Main Switchgear Room | Modbus RTU/IP gateway connection | Network | Modbus Power Meter (e.g. | BMS Contractor | BMS-01 BMS general spec — Electrical Max Demand Control; A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001 | Main 1 — refine after Q-011
ee.mtr-main-1.kw | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-1 | Main Switchgear Room | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001 | Modbus register
ee.mtr-main-1.kwh | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-1 | Main Switchgear Room | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-1.kvar | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-1 | Main Switchgear Room | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-1.v-avg | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-1 | Main Switchgear Room | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-1.i-avg | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-1 | Main Switchgear Room | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-2.network | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-2 | Main Switchgear Room | Modbus RTU/IP gateway connection | Network | Modbus Power Meter | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001 | Main 2 (e.g., Generator)
ee.mtr-main-2.kw | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-2 | Main Switchgear Room | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-2.kwh | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-2 | Main Switchgear Room | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-2.kvar | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-2 | Main Switchgear Room | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-2.v-avg | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-2 | Main Switchgear Room | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-2.i-avg | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-2 | Main Switchgear Room | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-3.network | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-3 | Main Switchgear Room | Modbus RTU/IP gateway connection | Network | Modbus Power Meter | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001 | Main 3 (e.g., ATS bus tie)
ee.mtr-main-3.kw | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-3 | Main Switchgear Room | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-3.kwh | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-3 | Main Switchgear Room | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-3.kvar | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-3 | Main Switchgear Room | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-3.v-avg | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-3 | Main Switchgear Room | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-main-3.i-avg | Power Metering | Multifunction Power Meter (Main) | MTR-MAIN-3 | Main Switchgear Room | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-MAIN | A-004 / A-EE-001
ee.mtr-fdr-01.network | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-01 | Distribution (per A4) | Modbus RTU/IP gateway connection | Network | Modbus Power Meter | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001 | Chiller plant feeder
ee.mtr-fdr-01.kw | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-01 | Distribution (per A4) | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-01.kwh | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-01 | Distribution (per A4) | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-01.kvar | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-01 | Distribution (per A4) | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-01.v-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-01 | Distribution (per A4) | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-01.i-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-01 | Distribution (per A4) | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-02.network | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-02 | Distribution (per A4) | Modbus RTU/IP gateway connection | Network | Modbus Power Meter | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001 | AHU plant feeder
ee.mtr-fdr-02.kw | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-02 | Distribution (per A4) | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-02.kwh | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-02 | Distribution (per A4) | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-02.kvar | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-02 | Distribution (per A4) | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-02.v-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-02 | Distribution (per A4) | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-02.i-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-02 | Distribution (per A4) | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-03.network | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-03 | Distribution (per A4) | Modbus RTU/IP gateway connection | Network | Modbus Power Meter | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001 | Kitchen feeder
ee.mtr-fdr-03.kw | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-03 | Distribution (per A4) | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-03.kwh | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-03 | Distribution (per A4) | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-03.kvar | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-03 | Distribution (per A4) | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-03.v-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-03 | Distribution (per A4) | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-03.i-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-03 | Distribution (per A4) | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-04.network | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-04 | Distribution (per A4) | Modbus RTU/IP gateway connection | Network | Modbus Power Meter | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001 | Lighting feeder
ee.mtr-fdr-04.kw | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-04 | Distribution (per A4) | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-04.kwh | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-04 | Distribution (per A4) | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-04.kvar | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-04 | Distribution (per A4) | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-04.v-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-04 | Distribution (per A4) | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-04.i-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-04 | Distribution (per A4) | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-05.network | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-05 | Distribution (per A4) | Modbus RTU/IP gateway connection | Network | Modbus Power Meter | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001 | Hotwater plant feeder
ee.mtr-fdr-05.kw | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-05 | Distribution (per A4) | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-05.kwh | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-05 | Distribution (per A4) | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-05.kvar | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-05 | Distribution (per A4) | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-05.v-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-05 | Distribution (per A4) | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-05.i-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-05 | Distribution (per A4) | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-06.network | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-06 | Distribution (per A4) | Modbus RTU/IP gateway connection | Network | Modbus Power Meter | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001 | Lifts feeder
ee.mtr-fdr-06.kw | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-06 | Distribution (per A4) | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-06.kwh | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-06 | Distribution (per A4) | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-06.kvar | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-06 | Distribution (per A4) | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-06.v-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-06 | Distribution (per A4) | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-06.i-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-06 | Distribution (per A4) | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-07.network | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-07 | Distribution (per A4) | Modbus RTU/IP gateway connection | Network | Modbus Power Meter | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001 | BMS UPS feeder
ee.mtr-fdr-07.kw | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-07 | Distribution (per A4) | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-07.kwh | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-07 | Distribution (per A4) | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-07.kvar | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-07 | Distribution (per A4) | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-07.v-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-07 | Distribution (per A4) | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-07.i-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-07 | Distribution (per A4) | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-08.network | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-08 | Distribution (per A4) | Modbus RTU/IP gateway connection | Network | Modbus Power Meter | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001 | Mechanical/Pumps feeder
ee.mtr-fdr-08.kw | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-08 | Distribution (per A4) | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-08.kwh | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-08 | Distribution (per A4) | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-08.kvar | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-08 | Distribution (per A4) | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-08.v-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-08 | Distribution (per A4) | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-08.i-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-08 | Distribution (per A4) | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-09.network | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-09 | Distribution (per A4) | Modbus RTU/IP gateway connection | Network | Modbus Power Meter | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001 | Boiler/Laundry feeder
ee.mtr-fdr-09.kw | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-09 | Distribution (per A4) | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-09.kwh | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-09 | Distribution (per A4) | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-09.kvar | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-09 | Distribution (per A4) | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-09.v-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-09 | Distribution (per A4) | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-09.i-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-09 | Distribution (per A4) | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-10.network | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-10 | Distribution (per A4) | Modbus RTU/IP gateway connection | Network | Modbus Power Meter | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001 | Fire pump feeder
ee.mtr-fdr-10.kw | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-10 | Distribution (per A4) | Active Power (kW total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-10.kwh | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-10 | Distribution (per A4) | Cumulative Energy (kWh total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-10.kvar | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-10 | Distribution (per A4) | Reactive Power (kVAR total) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-10.v-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-10 | Distribution (per A4) | Average Voltage (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001
ee.mtr-fdr-10.i-avg | Power Metering | Multifunction Power Meter (Feeder) | MTR-FDR-10 | Distribution (per A4) | Average Current (3-phase RMS) | HLI | - | BMS Contractor | A-EE-001 | PNL-EE-DIST | A-004 / A-EE-001