## Summary
A2 — Equipment Takeoff Summary
Total instances | 135
By equipment class
Exhaust Fan (General) | 34
Exhaust Fan (Toilet) | 34
Multifunction Power Meter (Feeder) | 10
Heat Pump | 6
Calorifier (Hot Water Storage Tank) | 6
Recirculating Pump | 6
Chiller (Package Water-Cooled) | 3
AHU (Chilled-Water-Served) | 3
Condenser Water Pump | 3
Cooling Tower | 3
DOAS Unit | 3
Multifunction Power Meter (Main) | 3
Primary CHW Pump | 3
AHU (Modulating CHW-served) | 2
Condenser Water Header | 2
Hot Water Header Set | 2
Ozone Generator (UV-light or Corona) | 2
Precooled Air Handling Unit | 2
Steam Boiler | 2
BTU Meter | 1
Cooling Tower (Common) | 1
CHW Bypass Header | 1
CHW Return Main Header | 1
CHW Supply Main Header | 1
Primary CHW Pump (Standby) | 1
By location
3rd Amenity & Guestroom | 27
Basement | 16
2nd Floor | 13
2F/CHW Pump Room | 11
Roofdeck/HW Plant | 10
Lower Ground/HW Plant | 10
Distribution (per A4) | 10
GF Main Lobby | 9
Roofdeck/Cooling Tower Area | 6
2nd Level/Casino MVAC Plant | 5
GND/Chiller Plant Room | 3
GND/BOH AHU Area | 3
Roofdeck | 3
Main Switchgear Room | 3
Roofdeck/Hotel DOAS Plant | 2
Roofdeck/PAHU Plant | 2
Lower Ground/Boiler Room | 2
By panel
PNL-VENT-L3 | 27
PNL-VENT-BSMT | 16
PNL-VENT-L2 | 13
PNL-CHWP-L2 | 11
PNL-PL-HZ | 10
PNL-PL-LZ | 10
PNL-EE-DIST | 10
PNL-VENT-GF | 9
PNL-CT-RD | 6
PNL-AHU-L2 | 4
PNL-CH-PLANT-GND | 3
PNL-CHWP-GND | 3
PNL-VENT-RD | 3
PNL-EE-MAIN | 3
PNL-DOAS-RD | 2
PNL-PAHU-RD | 2
PNL-BL-LZ | 2
PNL-DOAS-L2 | 1

## Equipment Takeoff
ID | Equipment Class | Quantity | Location | System | Panel | Primary C/O | Physical I/O | HLI Subpoints | Network Drops | Total I/O | Make/Model Assumed | Network Type | Typical Supplier | Notes
AHU-2M.1 | AHU (Modulating CHW-served) | 1 | 2nd Level/Casino MVAC Plant | AHU - Casino | PNL-AHU-L2 | BMS Contractor | 13 | 2 | 1 | 16 | Modulating CHW-served AHU with VFD, modulating valve and dampers (position feedback) | Hardwired (VFD via BACnet HLI) | Mechanical contractor | Casino-spec AHU — modulating actuators with position feedback; CO/CO2 monitoring at return duct.
AHU-2M.2 | AHU (Modulating CHW-served) | 1 | 2nd Level/Casino MVAC Plant | AHU - Casino | PNL-AHU-L2 | BMS Contractor | 13 | 2 | 1 | 16 | Modulating CHW-served AHU with VFD, modulating valve and dampers (position feedback) | Hardwired (VFD via BACnet HLI) | Mechanical contractor | Casino-spec AHU — modulating actuators with position feedback; CO/CO2 monitoring at return duct.
BTU-CHWS-MAIN | BTU Meter | 1 | 2F/CHW Pump Room | Chilled Water | PNL-CHWP-L2 | BMS Contractor | 0 | 3 | 1 | 4 | Ultrasonic or insertion-type BTU meter with Modbus output (Onicon, Aichi, Kamstrup) | Modbus RTU/TCP | BMS contractor | System-level energy submeter.
CH-1 | Chiller (Package Water-Cooled) | 1 | GND/Chiller Plant Room | Chilled Water | PNL-CH-PLANT-GND | Equipment Supplier | 9 | 18 | 1 | 28 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CH-2 | Chiller (Package Water-Cooled) | 1 | GND/Chiller Plant Room | Chilled Water | PNL-CH-PLANT-GND | Equipment Supplier | 9 | 18 | 1 | 28 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CH-3 | Chiller (Package Water-Cooled) | 1 | GND/Chiller Plant Room | Chilled Water | PNL-CH-PLANT-GND | Equipment Supplier | 9 | 18 | 1 | 28 | Tier-1 BACnet IP chiller (Trane/York/Carrier/Daikin), water-cooled centrifugal or screw, sized per design cooling load | BACnet/IP | Mechanical contractor / Equipment supplier | BMS reads via chiller's native BACnet gateway. BMS supplies external T-sensors on entering/leaving CHW & CW pipes.
CHWP-1.1 | AHU (Chilled-Water-Served) | 1 | GND/BOH AHU Area | BOH Air Handling | PNL-CHWP-GND | Equipment Supplier | 14 | 2 | 1 | 17 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
CHWP-1.2 | AHU (Chilled-Water-Served) | 1 | GND/BOH AHU Area | BOH Air Handling | PNL-CHWP-GND | Equipment Supplier | 14 | 2 | 1 | 17 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
CHWP-1.3 | AHU (Chilled-Water-Served) | 1 | GND/BOH AHU Area | BOH Air Handling | PNL-CHWP-GND | Equipment Supplier | 14 | 2 | 1 | 17 | Standard CHW-served AHU with VFD-driven supply fan, modulating CHW valve, and OA/RA dampers | Hardwired (VFD via BACnet HLI) | Mechanical contractor | BMS supplies sensors (T/RH/CO2). Dampers and CHW valve supplied by ME contractor. Fan + VFD by Equipment Supplier.
COMP-1 | Condenser Water Pump | 1 | 2F/CHW Pump Room | Chilled Water | PNL-CHWP-L2 | Equipment Supplier | 4 | 0 | 0 | 4 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
COMP-2 | Condenser Water Pump | 1 | 2F/CHW Pump Room | Chilled Water | PNL-CHWP-L2 | Equipment Supplier | 4 | 0 | 0 | 4 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
COMP-3 | Condenser Water Pump | 1 | 2F/CHW Pump Room | Chilled Water | PNL-CHWP-L2 | Equipment Supplier | 4 | 0 | 0 | 4 | End-suction or split-case centrifugal, fixed-speed (typical) or VFD (energy-conscious) | Hardwired | Mechanical contractor | BMS reads aux contacts; commands start via DO.
CT-1 | Cooling Tower | 1 | Roofdeck/Cooling Tower Area | Chilled Water | PNL-CT-RD | BMS Contractor | 9 | 0 | 0 | 9 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-2 | Cooling Tower | 1 | Roofdeck/Cooling Tower Area | Chilled Water | PNL-CT-RD | BMS Contractor | 9 | 0 | 0 | 9 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-3 | Cooling Tower | 1 | Roofdeck/Cooling Tower Area | Chilled Water | PNL-CT-RD | BMS Contractor | 9 | 0 | 0 | 9 | Induced-draft counterflow open cooling tower (Marley/BAC/EVAPCO), sized per condenser water flow | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies basin level sensors and condenser water header T-sensors.
CT-COMMON | Cooling Tower (Common) | 1 | Roofdeck/Cooling Tower Area | Chilled Water | PNL-CT-RD | BMS Contractor | 2 | 0 | 0 | 2 | Common BMS sensors at cooling tower area (OA T/RH, condenser headers) | Hardwired | BMS contractor | Field instrumentation only — no equipment per se.
DOAS-2W | DOAS Unit | 1 | 2nd Level/Casino MVAC Plant | DOAS - Casino MVAC | PNL-DOAS-L2 | Equipment Supplier | 21 | 4 | 1 | 26 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
DOAS-RD.1 | DOAS Unit | 1 | Roofdeck/Hotel DOAS Plant | DOAS - Hotel/Roofdeck | PNL-DOAS-RD | Equipment Supplier | 21 | 4 | 1 | 26 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
DOAS-RD.2 | DOAS Unit | 1 | Roofdeck/Hotel DOAS Plant | DOAS - Hotel/Roofdeck | PNL-DOAS-RD | Equipment Supplier | 21 | 4 | 1 | 26 | Dedicated Outdoor Air System with energy recovery wheel, supply + exhaust fans, CHW coil | BACnet/IP | Mechanical contractor / Equipment supplier | Native BACnet controller typical. BMS supplies external sensors (OA T/RH/Flow, indoor T/RH, exhaust T) and modulating valve actuator.
EF-1 (RD) | Exhaust Fan (General) | 1 | Roofdeck | General Ventilation | PNL-VENT-RD | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-1.2A | Exhaust Fan (General) | 1 | GF Main Lobby | General Ventilation | PNL-VENT-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-1MR.1 | Exhaust Fan (General) | 1 | GF Main Lobby | General Ventilation | PNL-VENT-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-1ST0.1 | Exhaust Fan (General) | 1 | GF Main Lobby | General Ventilation | PNL-VENT-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2.1 | Exhaust Fan (General) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2.2 | Exhaust Fan (General) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2.3 | Exhaust Fan (General) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2.4 | Exhaust Fan (General) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2B.1 | Exhaust Fan (General) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-2B.2 | Exhaust Fan (General) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-3.1 | Exhaust Fan (General) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-3.2 | Exhaust Fan (General) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-3SF.2 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-8R.1 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-B.1 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-B.2 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-BS.1 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-BS.2 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-CHR.1 | Exhaust Fan (General) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-CHR.2 | Exhaust Fan (General) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-GLZ.1 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-GLZ.2 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-GS.1 | Exhaust Fan (General) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-GS.2 | Exhaust Fan (General) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-HP.1 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-LPG.1 | Exhaust Fan (General) | 1 | GF Main Lobby | General Ventilation | PNL-VENT-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-MC.1 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-MFP.1 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-MRF.1 | Exhaust Fan (General) | 1 | GF Main Lobby | General Ventilation | PNL-VENT-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-PR.1 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-PR.2 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-RD.1 | Exhaust Fan (General) | 1 | Roofdeck | General Ventilation | PNL-VENT-RD | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-RD.2 | Exhaust Fan (General) | 1 | Roofdeck | General Ventilation | PNL-VENT-RD | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
EF-RR.2 | Exhaust Fan (General) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line, ceiling, or roof-mounted general exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
HDR-CHW-BP | CHW Bypass Header | 1 | 2F/CHW Pump Room | Chilled Water | PNL-CHWP-L2 | BMS Contractor | 4 | 0 | 0 | 4 | BMS dP/dT sensors + motorized bypass valve (BMS-supplied) | Hardwired | BMS contractor | BMS controls bypass valve to maintain CHW differential.
HDR-CHWR | CHW Return Main Header | 1 | 2F/CHW Pump Room | Chilled Water | PNL-CHWP-L2 | BMS Contractor | 2 | 0 | 0 | 2 | BMS T+P sensors on CHW return manifold | Hardwired | BMS contractor | Field instrumentation only.
HDR-CHWS | CHW Supply Main Header | 1 | 2F/CHW Pump Room | Chilled Water | PNL-CHWP-L2 | BMS Contractor | 2 | 0 | 0 | 2 | BMS T+P sensors on CHW supply manifold | Hardwired | BMS contractor | Field instrumentation only.
HDR-CWR-RD | Condenser Water Header | 1 | Roofdeck/Cooling Tower Area | Chilled Water | PNL-CT-RD | BMS Contractor | 1 | 0 | 0 | 1 | BMS T sensors on condenser water headers at roofdeck | Hardwired | BMS contractor | Field instrumentation only.
HDR-CWS-RD | Condenser Water Header | 1 | Roofdeck/Cooling Tower Area | Chilled Water | PNL-CT-RD | BMS Contractor | 1 | 0 | 0 | 1 | BMS T sensors on condenser water headers at roofdeck | Hardwired | BMS contractor | Field instrumentation only.
HDR-HW-HZ | Hot Water Header Set | 1 | Roofdeck/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-HZ | BMS Contractor | 3 | 0 | 0 | 3 | Hot water supply/return manifolds with BMS T sensors and make-up cold water T sensor | Hardwired | BMS contractor | Field instrumentation on existing piping.
HDR-HW-LZ | Hot Water Header Set | 1 | Lower Ground/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-LZ | BMS Contractor | 3 | 0 | 0 | 3 | Hot water supply/return manifolds with BMS T sensors and make-up cold water T sensor | Hardwired | BMS contractor | Field instrumentation on existing piping.
HP-HZ-1 | Heat Pump | 1 | Roofdeck/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-HZ | Equipment Supplier | 0 | 3 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-HZ-2 | Heat Pump | 1 | Roofdeck/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-HZ | Equipment Supplier | 0 | 3 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-HZ-3 | Heat Pump | 1 | Roofdeck/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-HZ | Equipment Supplier | 0 | 3 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-LZ-1 | Heat Pump | 1 | Lower Ground/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-LZ | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-LZ-2 | Heat Pump | 1 | Lower Ground/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-LZ | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HP-LZ-3 | Heat Pump | 1 | Lower Ground/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-LZ | Equipment Supplier | 3 | 0 | 0 | 3 | Air-source or water-source heat pump for hot water heating | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor / Equipment supplier | BMS reads pump status/HOA/trip via aux contacts.
HWT-HZ-1 | Calorifier (Hot Water Storage Tank) | 1 | Roofdeck/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-HZ | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-HZ-2 | Calorifier (Hot Water Storage Tank) | 1 | Roofdeck/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-HZ | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-HZ-3 | Calorifier (Hot Water Storage Tank) | 1 | Roofdeck/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-HZ | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-LZ-1 | Calorifier (Hot Water Storage Tank) | 1 | Lower Ground/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-LZ | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-LZ-2 | Calorifier (Hot Water Storage Tank) | 1 | Lower Ground/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-LZ | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
HWT-LZ-3 | Calorifier (Hot Water Storage Tank) | 1 | Lower Ground/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-LZ | BMS Contractor | 1 | 0 | 0 | 1 | Pressurised hot-water storage tank with internal coil, sized per design hot water demand | Hardwired | Plumbing contractor | BMS supplies tank temperature sensor (immersion or strapped probe).
MTR-FDR-01 | Multifunction Power Meter (Feeder) | 1 | Distribution (per A4) | Power Metering | PNL-EE-DIST | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MTR-FDR-02 | Multifunction Power Meter (Feeder) | 1 | Distribution (per A4) | Power Metering | PNL-EE-DIST | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MTR-FDR-03 | Multifunction Power Meter (Feeder) | 1 | Distribution (per A4) | Power Metering | PNL-EE-DIST | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MTR-FDR-04 | Multifunction Power Meter (Feeder) | 1 | Distribution (per A4) | Power Metering | PNL-EE-DIST | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MTR-FDR-05 | Multifunction Power Meter (Feeder) | 1 | Distribution (per A4) | Power Metering | PNL-EE-DIST | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MTR-FDR-06 | Multifunction Power Meter (Feeder) | 1 | Distribution (per A4) | Power Metering | PNL-EE-DIST | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MTR-FDR-07 | Multifunction Power Meter (Feeder) | 1 | Distribution (per A4) | Power Metering | PNL-EE-DIST | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MTR-FDR-08 | Multifunction Power Meter (Feeder) | 1 | Distribution (per A4) | Power Metering | PNL-EE-DIST | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MTR-FDR-09 | Multifunction Power Meter (Feeder) | 1 | Distribution (per A4) | Power Metering | PNL-EE-DIST | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MTR-FDR-10 | Multifunction Power Meter (Feeder) | 1 | Distribution (per A4) | Power Metering | PNL-EE-DIST | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output, sub-feeder class (smaller form factor) | Modbus RTU | BMS contractor | Daisy-chained on Modbus bus(es) back to BMS gateway.
MTR-MAIN-1 | Multifunction Power Meter (Main) | 1 | Main Switchgear Room | Power Metering | PNL-EE-MAIN | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output (Schneider PM-series, ABB M2M, Siemens SENTRON), main switchgear class | Modbus RTU/TCP | BMS contractor | Mounted in main switchgear or on dedicated BMS-side panel.
MTR-MAIN-2 | Multifunction Power Meter (Main) | 1 | Main Switchgear Room | Power Metering | PNL-EE-MAIN | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output (Schneider PM-series, ABB M2M, Siemens SENTRON), main switchgear class | Modbus RTU/TCP | BMS contractor | Mounted in main switchgear or on dedicated BMS-side panel.
MTR-MAIN-3 | Multifunction Power Meter (Main) | 1 | Main Switchgear Room | Power Metering | PNL-EE-MAIN | BMS Contractor | 0 | 5 | 1 | 6 | Multifunction power meter with Modbus output (Schneider PM-series, ABB M2M, Siemens SENTRON), main switchgear class | Modbus RTU/TCP | BMS contractor | Mounted in main switchgear or on dedicated BMS-side panel.
OZ-2M.1 | Ozone Generator (UV-light or Corona) | 1 | 2nd Level/Casino MVAC Plant | AHU - Casino (Ozonizer) | PNL-AHU-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | UV-light or corona-discharge ozone generator (paired with Casino AHU) | Hardwired | Equipment supplier | Casino-specific air-treatment device. BMS monitors status/trip and reads VOC sensor (BMS-supplied).
OZ-2M.2 | Ozone Generator (UV-light or Corona) | 1 | 2nd Level/Casino MVAC Plant | AHU - Casino (Ozonizer) | PNL-AHU-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | UV-light or corona-discharge ozone generator (paired with Casino AHU) | Hardwired | Equipment supplier | Casino-specific air-treatment device. BMS monitors status/trip and reads VOC sensor (BMS-supplied).
PAHU-RD.1 | Precooled Air Handling Unit | 1 | Roofdeck/PAHU Plant | PAHU - Roofdeck | PNL-PAHU-RD | Equipment Supplier | 11 | 2 | 1 | 14 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PAHU-RD.2 | Precooled Air Handling Unit | 1 | Roofdeck/PAHU Plant | PAHU - Roofdeck | PNL-PAHU-RD | Equipment Supplier | 11 | 2 | 1 | 14 | Precool AHU at Roofdeck with CHW coil, VFD-driven fresh air fan; no exhaust path | Hardwired (VFD via BACnet HLI) | Mechanical contractor / Equipment supplier | Precool function: cools outdoor air before it's distributed to other systems. BMS supplies OA/supply T sensors.
PCHWP-1 | Primary CHW Pump | 1 | 2F/CHW Pump Room | Chilled Water | PNL-CHWP-L2 | Equipment Supplier | 5 | 0 | 0 | 5 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
PCHWP-2 | Primary CHW Pump | 1 | 2F/CHW Pump Room | Chilled Water | PNL-CHWP-L2 | Equipment Supplier | 5 | 0 | 0 | 5 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
PCHWP-3 | Primary CHW Pump | 1 | 2F/CHW Pump Room | Chilled Water | PNL-CHWP-L2 | Equipment Supplier | 5 | 0 | 0 | 5 | End-suction or split-case centrifugal with VFD, sized per design CHW flow | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | VFD typically Equipment Supplier provided with BACnet card.
PCHWP-4 | Primary CHW Pump (Standby) | 1 | 2F/CHW Pump Room | Chilled Water | PNL-CHWP-L2 | Equipment Supplier | 5 | 0 | 0 | 5 | Same as Primary CHW Pump (1 standby for N+1 redundancy) | Hardwired (BMS reads VFD via BACnet HLI) | Mechanical contractor | Standby unit per A-CHW-001.
RP-HZ-1 | Recirculating Pump | 1 | Roofdeck/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-HZ | Equipment Supplier | 0 | 3 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-HZ-2 | Recirculating Pump | 1 | Roofdeck/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-HZ | Equipment Supplier | 0 | 3 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-HZ-3 | Recirculating Pump | 1 | Roofdeck/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-HZ | Equipment Supplier | 0 | 3 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-LZ-1 | Recirculating Pump | 1 | Lower Ground/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-LZ | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-LZ-2 | Recirculating Pump | 1 | Lower Ground/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-LZ | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
RP-LZ-3 | Recirculating Pump | 1 | Lower Ground/HW Plant | Plumbing & Sanitary Hotwater | PNL-PL-LZ | Equipment Supplier | 3 | 0 | 0 | 3 | Hot water recirculating pump, fixed-speed (typical for hotwater systems) | Hardwired (LZ) or HLI (HZ — per A-PL-001) | Plumbing contractor | BMS reads aux contacts only.
SB-1 | Steam Boiler | 1 | Lower Ground/Boiler Room | Boiler/Laundry | PNL-BL-LZ | Equipment Supplier | 16 | 0 | 0 | 16 | Fire-tube steam boiler with multi-stage burner, fuel-oil fired (typical for hotel laundry) | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies steam pressure, feedwater T, fluegas T+O2 sensors. Boiler equipment provides aux contacts for status/HOA/trip points.
SB-2 | Steam Boiler | 1 | Lower Ground/Boiler Room | Boiler/Laundry | PNL-BL-LZ | Equipment Supplier | 16 | 0 | 0 | 16 | Fire-tube steam boiler with multi-stage burner, fuel-oil fired (typical for hotel laundry) | Hardwired | Mechanical contractor / Equipment supplier | BMS supplies steam pressure, feedwater T, fluegas T+O2 sensors. Boiler equipment provides aux contacts for status/HOA/trip points.
TEF-1.1 | Exhaust Fan (Toilet) | 1 | GF Main Lobby | General Ventilation | PNL-VENT-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-1.2 | Exhaust Fan (Toilet) | 1 | GF Main Lobby | General Ventilation | PNL-VENT-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-1.3 | Exhaust Fan (Toilet) | 1 | GF Main Lobby | General Ventilation | PNL-VENT-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-1.4 | Exhaust Fan (Toilet) | 1 | GF Main Lobby | General Ventilation | PNL-VENT-GF | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2.1 | Exhaust Fan (Toilet) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2.3 | Exhaust Fan (Toilet) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-2B.3 | Exhaust Fan (Toilet) | 1 | 2nd Floor | General Ventilation | PNL-VENT-L2 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3A.1 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3A.2 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3B | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3C.1 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3C.2 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.1 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.10 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.11 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.12 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.13 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.14 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.15 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.16 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.17 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.18 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.19 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.2 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.20 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.3 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.4 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.5 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.6 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.7 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.8 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-3D.9 | Exhaust Fan (Toilet) | 1 | 3rd Amenity & Guestroom | General Ventilation | PNL-VENT-L3 | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.1 | Exhaust Fan (Toilet) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.
TEF-B.2 | Exhaust Fan (Toilet) | 1 | Basement | General Ventilation | PNL-VENT-BSMT | Equipment Supplier | 3 | 0 | 0 | 3 | Constant-speed in-line or roof-mounted toilet exhaust fan | Hardwired | Mechanical contractor | BMS reads aux contacts only — no control points.