## Summary
A3 — Cable Schedule Summary
Total field cable runs | 175
Total field cable length (m) | 5250
Total trunk cable length (m) | 1020
Total power feed length (m) | 540
GRAND TOTAL cable length (m) | 6810
By cable type (m)
4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 2940
4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 1020
Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 810
4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 480

## Field Cables
ID | From | To | Equipment Class | System | Location | Cable Type | Conductors Required | Conductors Specified | Length (m) | I/O Points Carried | Notes
C0001 | PNL-AHU-L2 | AHU-2M.1 (BMS Contractor) | AHU (Modulating CHW-served) | AHU - Casino | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0002 | PNL-AHU-L2 | AHU-2M.1 (Equipment Supplier) | AHU (Modulating CHW-served) | AHU - Casino | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0003 | PNL-AHU-L2 | AHU-2M.1 (ME Contractor) | AHU (Modulating CHW-served) | AHU - Casino | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0004 | PNL-AHU-L2 | AHU-2M.2 (BMS Contractor) | AHU (Modulating CHW-served) | AHU - Casino | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0005 | PNL-AHU-L2 | AHU-2M.2 (Equipment Supplier) | AHU (Modulating CHW-served) | AHU - Casino | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0006 | PNL-AHU-L2 | AHU-2M.2 (ME Contractor) | AHU (Modulating CHW-served) | AHU - Casino | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0007 | PNL-CH-PLANT-GND | CH-1 (BMS Contractor) | Chiller (Package Water-Cooled) | Chilled Water | GND/Chiller Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 9 | 12 | 30 | 7 | 7 I/O points carried, 12C cable; length 30 m (legacy_fallback)
C0008 | PNL-CH-PLANT-GND | CH-1 (ME Contractor) | Chiller (Package Water-Cooled) | Chilled Water | GND/Chiller Plant Room | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0009 | PNL-CH-PLANT-GND | CH-2 (BMS Contractor) | Chiller (Package Water-Cooled) | Chilled Water | GND/Chiller Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 9 | 12 | 30 | 7 | 7 I/O points carried, 12C cable; length 30 m (legacy_fallback)
C0010 | PNL-CH-PLANT-GND | CH-2 (ME Contractor) | Chiller (Package Water-Cooled) | Chilled Water | GND/Chiller Plant Room | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0011 | PNL-CH-PLANT-GND | CH-3 (BMS Contractor) | Chiller (Package Water-Cooled) | Chilled Water | GND/Chiller Plant Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 9 | 12 | 30 | 7 | 7 I/O points carried, 12C cable; length 30 m (legacy_fallback)
C0012 | PNL-CH-PLANT-GND | CH-3 (ME Contractor) | Chiller (Package Water-Cooled) | Chilled Water | GND/Chiller Plant Room | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0013 | PNL-CHWP-GND | CHWP-1.1 (BMS Contractor) | AHU (Chilled-Water-Served) | BOH Air Handling | GND/BOH AHU Area | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0014 | PNL-CHWP-GND | CHWP-1.1 (Equipment Supplier) | AHU (Chilled-Water-Served) | BOH Air Handling | GND/BOH AHU Area | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0015 | PNL-CHWP-GND | CHWP-1.1 (ME Contractor) | AHU (Chilled-Water-Served) | BOH Air Handling | GND/BOH AHU Area | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0016 | PNL-CHWP-GND | CHWP-1.2 (BMS Contractor) | AHU (Chilled-Water-Served) | BOH Air Handling | GND/BOH AHU Area | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0017 | PNL-CHWP-GND | CHWP-1.2 (Equipment Supplier) | AHU (Chilled-Water-Served) | BOH Air Handling | GND/BOH AHU Area | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0018 | PNL-CHWP-GND | CHWP-1.2 (ME Contractor) | AHU (Chilled-Water-Served) | BOH Air Handling | GND/BOH AHU Area | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0019 | PNL-CHWP-GND | CHWP-1.3 (BMS Contractor) | AHU (Chilled-Water-Served) | BOH Air Handling | GND/BOH AHU Area | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0020 | PNL-CHWP-GND | CHWP-1.3 (Equipment Supplier) | AHU (Chilled-Water-Served) | BOH Air Handling | GND/BOH AHU Area | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0021 | PNL-CHWP-GND | CHWP-1.3 (ME Contractor) | AHU (Chilled-Water-Served) | BOH Air Handling | GND/BOH AHU Area | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0022 | PNL-CHWP-L2 | COMP-1 (Equipment Supplier) | Condenser Water Pump | Chilled Water | 2F/CHW Pump Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0023 | PNL-CHWP-L2 | COMP-2 (Equipment Supplier) | Condenser Water Pump | Chilled Water | 2F/CHW Pump Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0024 | PNL-CHWP-L2 | COMP-3 (Equipment Supplier) | Condenser Water Pump | Chilled Water | 2F/CHW Pump Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0025 | PNL-CT-RD | CT-1 (BMS Contractor) | Cooling Tower | Chilled Water | Roofdeck/Cooling Tower Area | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0026 | PNL-CT-RD | CT-1 (Equipment Supplier) | Cooling Tower | Chilled Water | Roofdeck/Cooling Tower Area | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0027 | PNL-CT-RD | CT-1 (ME Contractor) | Cooling Tower | Chilled Water | Roofdeck/Cooling Tower Area | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0028 | PNL-CT-RD | CT-2 (BMS Contractor) | Cooling Tower | Chilled Water | Roofdeck/Cooling Tower Area | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0029 | PNL-CT-RD | CT-2 (Equipment Supplier) | Cooling Tower | Chilled Water | Roofdeck/Cooling Tower Area | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0030 | PNL-CT-RD | CT-2 (ME Contractor) | Cooling Tower | Chilled Water | Roofdeck/Cooling Tower Area | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0031 | PNL-CT-RD | CT-3 (BMS Contractor) | Cooling Tower | Chilled Water | Roofdeck/Cooling Tower Area | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0032 | PNL-CT-RD | CT-3 (Equipment Supplier) | Cooling Tower | Chilled Water | Roofdeck/Cooling Tower Area | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0033 | PNL-CT-RD | CT-3 (ME Contractor) | Cooling Tower | Chilled Water | Roofdeck/Cooling Tower Area | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0034 | PNL-CT-RD | CT-COMMON (BMS Contractor) | Cooling Tower (Common) | Chilled Water | Roofdeck/Cooling Tower Area | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0035 | PNL-DOAS-L2 | DOAS-2W (BMS Contractor) | DOAS Unit | DOAS - Casino MVAC | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 11 | 12 | 30 | 9 | 9 I/O points carried, 12C cable; length 30 m (legacy_fallback)
C0036 | PNL-DOAS-L2 | DOAS-2W (Equipment Supplier) | DOAS Unit | DOAS - Casino MVAC | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 10 | 12 | 30 | 8 | 8 I/O points carried, 12C cable; length 30 m (legacy_fallback)
C0037 | PNL-DOAS-L2 | DOAS-2W (ME Contractor) | DOAS Unit | DOAS - Casino MVAC | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0038 | PNL-DOAS-RD | DOAS-RD.1 (BMS Contractor) | DOAS Unit | DOAS - Hotel/Roofdeck | Roofdeck/Hotel DOAS Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 11 | 12 | 30 | 9 | 9 I/O points carried, 12C cable; length 30 m (legacy_fallback)
C0039 | PNL-DOAS-RD | DOAS-RD.1 (Equipment Supplier) | DOAS Unit | DOAS - Hotel/Roofdeck | Roofdeck/Hotel DOAS Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 10 | 12 | 30 | 8 | 8 I/O points carried, 12C cable; length 30 m (legacy_fallback)
C0040 | PNL-DOAS-RD | DOAS-RD.1 (ME Contractor) | DOAS Unit | DOAS - Hotel/Roofdeck | Roofdeck/Hotel DOAS Plant | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0041 | PNL-DOAS-RD | DOAS-RD.2 (BMS Contractor) | DOAS Unit | DOAS - Hotel/Roofdeck | Roofdeck/Hotel DOAS Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 11 | 12 | 30 | 9 | 9 I/O points carried, 12C cable; length 30 m (legacy_fallback)
C0042 | PNL-DOAS-RD | DOAS-RD.2 (Equipment Supplier) | DOAS Unit | DOAS - Hotel/Roofdeck | Roofdeck/Hotel DOAS Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 10 | 12 | 30 | 8 | 8 I/O points carried, 12C cable; length 30 m (legacy_fallback)
C0043 | PNL-DOAS-RD | DOAS-RD.2 (ME Contractor) | DOAS Unit | DOAS - Hotel/Roofdeck | Roofdeck/Hotel DOAS Plant | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0044 | PNL-VENT-RD | EF-1 (RD) (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0045 | PNL-VENT-GF | EF-1.2A (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | GF Main Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0046 | PNL-VENT-GF | EF-1MR.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | GF Main Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0047 | PNL-VENT-GF | EF-1ST0.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | GF Main Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0048 | PNL-VENT-L2 | EF-2.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0049 | PNL-VENT-L2 | EF-2.2 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0050 | PNL-VENT-L2 | EF-2.3 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0051 | PNL-VENT-L2 | EF-2.4 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0052 | PNL-VENT-L2 | EF-2B.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0053 | PNL-VENT-L2 | EF-2B.2 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0054 | PNL-VENT-L3 | EF-3.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0055 | PNL-VENT-L3 | EF-3.2 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0056 | PNL-VENT-BSMT | EF-3SF.2 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0057 | PNL-VENT-BSMT | EF-8R.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0058 | PNL-VENT-BSMT | EF-B.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0059 | PNL-VENT-BSMT | EF-B.2 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0060 | PNL-VENT-BSMT | EF-BS.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0061 | PNL-VENT-BSMT | EF-BS.2 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0062 | PNL-VENT-L2 | EF-CHR.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0063 | PNL-VENT-L2 | EF-CHR.2 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0064 | PNL-VENT-BSMT | EF-GLZ.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0065 | PNL-VENT-BSMT | EF-GLZ.2 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0066 | PNL-VENT-L2 | EF-GS.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0067 | PNL-VENT-L2 | EF-GS.2 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0068 | PNL-VENT-BSMT | EF-HP.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0069 | PNL-VENT-GF | EF-LPG.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | GF Main Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0070 | PNL-VENT-BSMT | EF-MC.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0071 | PNL-VENT-BSMT | EF-MFP.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0072 | PNL-VENT-GF | EF-MRF.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | GF Main Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0073 | PNL-VENT-BSMT | EF-PR.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0074 | PNL-VENT-BSMT | EF-PR.2 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0075 | PNL-VENT-RD | EF-RD.1 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0076 | PNL-VENT-RD | EF-RD.2 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Roofdeck | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0077 | PNL-VENT-BSMT | EF-RR.2 (Equipment Supplier) | Exhaust Fan (General) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0078 | PNL-CHWP-L2 | HDR-CHW-BP (BMS Contractor) | CHW Bypass Header | Chilled Water | 2F/CHW Pump Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0079 | PNL-CHWP-L2 | HDR-CHWR (BMS Contractor) | CHW Return Main Header | Chilled Water | 2F/CHW Pump Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0080 | PNL-CHWP-L2 | HDR-CHWS (BMS Contractor) | CHW Supply Main Header | Chilled Water | 2F/CHW Pump Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0081 | PNL-CT-RD | HDR-CWR-RD (BMS Contractor) | Condenser Water Header | Chilled Water | Roofdeck/Cooling Tower Area | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0082 | PNL-CT-RD | HDR-CWS-RD (BMS Contractor) | Condenser Water Header | Chilled Water | Roofdeck/Cooling Tower Area | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0083 | PNL-PL-HZ | HDR-HW-HZ (BMS Contractor) | Hot Water Header Set | Plumbing & Sanitary Hotwater | Roofdeck/HW Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0084 | PNL-PL-LZ | HDR-HW-LZ (BMS Contractor) | Hot Water Header Set | Plumbing & Sanitary Hotwater | Lower Ground/HW Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0085 | PNL-PL-LZ | HP-LZ-1 (Equipment Supplier) | Heat Pump | Plumbing & Sanitary Hotwater | Lower Ground/HW Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0086 | PNL-PL-LZ | HP-LZ-2 (Equipment Supplier) | Heat Pump | Plumbing & Sanitary Hotwater | Lower Ground/HW Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0087 | PNL-PL-LZ | HP-LZ-3 (Equipment Supplier) | Heat Pump | Plumbing & Sanitary Hotwater | Lower Ground/HW Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0088 | PNL-PL-HZ | HWT-HZ-1 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | Plumbing & Sanitary Hotwater | Roofdeck/HW Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0089 | PNL-PL-HZ | HWT-HZ-2 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | Plumbing & Sanitary Hotwater | Roofdeck/HW Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0090 | PNL-PL-HZ | HWT-HZ-3 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | Plumbing & Sanitary Hotwater | Roofdeck/HW Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0091 | PNL-PL-LZ | HWT-LZ-1 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | Plumbing & Sanitary Hotwater | Lower Ground/HW Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0092 | PNL-PL-LZ | HWT-LZ-2 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | Plumbing & Sanitary Hotwater | Lower Ground/HW Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0093 | PNL-PL-LZ | HWT-LZ-3 (BMS Contractor) | Calorifier (Hot Water Storage Tank) | Plumbing & Sanitary Hotwater | Lower Ground/HW Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0094 | PNL-AHU-L2 | OZ-2M.1 (BMS Contractor) | Ozone Generator (UV-light or Corona) | AHU - Casino (Ozonizer) | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0095 | PNL-AHU-L2 | OZ-2M.1 (Equipment Supplier) | Ozone Generator (UV-light or Corona) | AHU - Casino (Ozonizer) | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0096 | PNL-AHU-L2 | OZ-2M.2 (BMS Contractor) | Ozone Generator (UV-light or Corona) | AHU - Casino (Ozonizer) | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0097 | PNL-AHU-L2 | OZ-2M.2 (Equipment Supplier) | Ozone Generator (UV-light or Corona) | AHU - Casino (Ozonizer) | 2nd Level/Casino MVAC Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 4 | 4 | 30 | 2 | 2 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0098 | PNL-PAHU-RD | PAHU-RD.1 (BMS Contractor) | Precooled Air Handling Unit | PAHU - Roofdeck | Roofdeck/PAHU Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0099 | PNL-PAHU-RD | PAHU-RD.1 (Equipment Supplier) | Precooled Air Handling Unit | PAHU - Roofdeck | Roofdeck/PAHU Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0100 | PNL-PAHU-RD | PAHU-RD.1 (ME Contractor) | Precooled Air Handling Unit | PAHU - Roofdeck | Roofdeck/PAHU Plant | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0101 | PNL-PAHU-RD | PAHU-RD.2 (BMS Contractor) | Precooled Air Handling Unit | PAHU - Roofdeck | Roofdeck/PAHU Plant | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 6 | 6 | 30 | 4 | 4 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0102 | PNL-PAHU-RD | PAHU-RD.2 (Equipment Supplier) | Precooled Air Handling Unit | PAHU - Roofdeck | Roofdeck/PAHU Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0103 | PNL-PAHU-RD | PAHU-RD.2 (ME Contractor) | Precooled Air Handling Unit | PAHU - Roofdeck | Roofdeck/PAHU Plant | 4C × 1.5 mm² FRLS (ME-supplied valves/dampers — status + control) | 3 | 4 | 30 | 1 | 1 I/O points carried, 4C cable; length 30 m (legacy_fallback)
C0104 | PNL-CHWP-L2 | PCHWP-1 (Equipment Supplier) | Primary CHW Pump | Chilled Water | 2F/CHW Pump Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0105 | PNL-CHWP-L2 | PCHWP-2 (Equipment Supplier) | Primary CHW Pump | Chilled Water | 2F/CHW Pump Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0106 | PNL-CHWP-L2 | PCHWP-3 (Equipment Supplier) | Primary CHW Pump | Chilled Water | 2F/CHW Pump Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0107 | PNL-CHWP-L2 | PCHWP-4 (Equipment Supplier) | Primary CHW Pump (Standby) | Chilled Water | 2F/CHW Pump Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 7 | 8 | 30 | 5 | 5 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0108 | PNL-PL-LZ | RP-LZ-1 (Equipment Supplier) | Recirculating Pump | Plumbing & Sanitary Hotwater | Lower Ground/HW Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0109 | PNL-PL-LZ | RP-LZ-2 (Equipment Supplier) | Recirculating Pump | Plumbing & Sanitary Hotwater | Lower Ground/HW Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0110 | PNL-PL-LZ | RP-LZ-3 (Equipment Supplier) | Recirculating Pump | Plumbing & Sanitary Hotwater | Lower Ground/HW Plant | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0111 | PNL-BL-LZ | SB-1 (BMS Contractor) | Steam Boiler | Boiler/Laundry | Lower Ground/Boiler Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0112 | PNL-BL-LZ | SB-1 (Equipment Supplier) | Steam Boiler | Boiler/Laundry | Lower Ground/Boiler Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | 12 | 30 | 10 | 10 I/O points carried, 12C cable; length 30 m (legacy_fallback)
C0113 | PNL-BL-LZ | SB-2 (BMS Contractor) | Steam Boiler | Boiler/Laundry | Lower Ground/Boiler Room | 4C × 1.5 mm² shielded FRLS (BMS signal — sensors) | 8 | 8 | 30 | 6 | 6 I/O points carried, 8C cable; length 30 m (legacy_fallback)
C0114 | PNL-BL-LZ | SB-2 (Equipment Supplier) | Steam Boiler | Boiler/Laundry | Lower Ground/Boiler Room | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 12 | 12 | 30 | 10 | 10 I/O points carried, 12C cable; length 30 m (legacy_fallback)
C0115 | PNL-VENT-GF | TEF-1.1 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | GF Main Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0116 | PNL-VENT-GF | TEF-1.2 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | GF Main Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0117 | PNL-VENT-GF | TEF-1.3 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | GF Main Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0118 | PNL-VENT-GF | TEF-1.4 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | GF Main Lobby | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0119 | PNL-VENT-L2 | TEF-2.1 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0120 | PNL-VENT-L2 | TEF-2.3 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0121 | PNL-VENT-L2 | TEF-2B.3 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 2nd Floor | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0122 | PNL-VENT-L3 | TEF-3A.1 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0123 | PNL-VENT-L3 | TEF-3A.2 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0124 | PNL-VENT-L3 | TEF-3B (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0125 | PNL-VENT-L3 | TEF-3C.1 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0126 | PNL-VENT-L3 | TEF-3C.2 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0127 | PNL-VENT-L3 | TEF-3D.1 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0128 | PNL-VENT-L3 | TEF-3D.10 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0129 | PNL-VENT-L3 | TEF-3D.11 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0130 | PNL-VENT-L3 | TEF-3D.12 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0131 | PNL-VENT-L3 | TEF-3D.13 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0132 | PNL-VENT-L3 | TEF-3D.14 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0133 | PNL-VENT-L3 | TEF-3D.15 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0134 | PNL-VENT-L3 | TEF-3D.16 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0135 | PNL-VENT-L3 | TEF-3D.17 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0136 | PNL-VENT-L3 | TEF-3D.18 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0137 | PNL-VENT-L3 | TEF-3D.19 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0138 | PNL-VENT-L3 | TEF-3D.2 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0139 | PNL-VENT-L3 | TEF-3D.20 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0140 | PNL-VENT-L3 | TEF-3D.3 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0141 | PNL-VENT-L3 | TEF-3D.4 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0142 | PNL-VENT-L3 | TEF-3D.5 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0143 | PNL-VENT-L3 | TEF-3D.6 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0144 | PNL-VENT-L3 | TEF-3D.7 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0145 | PNL-VENT-L3 | TEF-3D.8 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0146 | PNL-VENT-L3 | TEF-3D.9 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | 3rd Amenity & Guestroom | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0147 | PNL-VENT-BSMT | TEF-B.1 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0148 | PNL-VENT-BSMT | TEF-B.2 (Equipment Supplier) | Exhaust Fan (Toilet) | General Ventilation | Basement | 4C × 1.5 mm² FRLS (equipment aux contacts — status/HOA/trip) | 5 | 6 | 30 | 3 | 3 I/O points carried, 6C cable; length 30 m (legacy_fallback)
C0149 | PNL-CH-PLANT-GND | CH-1 (Network) | Chiller (Package Water-Cooled) | Chilled Water | GND/Chiller Plant Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0150 | PNL-CH-PLANT-GND | CH-2 (Network) | Chiller (Package Water-Cooled) | Chilled Water | GND/Chiller Plant Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0151 | PNL-CH-PLANT-GND | CH-3 (Network) | Chiller (Package Water-Cooled) | Chilled Water | GND/Chiller Plant Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0152 | PNL-CHWP-L2 | BTU-CHWS-MAIN (Network) | BTU Meter | Chilled Water | 2F/CHW Pump Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0153 | PNL-CHWP-GND | CHWP-1.1 (Network) | AHU (Chilled-Water-Served) | BOH Air Handling | GND/BOH AHU Area | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0154 | PNL-CHWP-GND | CHWP-1.2 (Network) | AHU (Chilled-Water-Served) | BOH Air Handling | GND/BOH AHU Area | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0155 | PNL-CHWP-GND | CHWP-1.3 (Network) | AHU (Chilled-Water-Served) | BOH Air Handling | GND/BOH AHU Area | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0156 | PNL-DOAS-L2 | DOAS-2W (Network) | DOAS Unit | DOAS - Casino MVAC | 2nd Level/Casino MVAC Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0157 | PNL-DOAS-RD | DOAS-RD.1 (Network) | DOAS Unit | DOAS - Hotel/Roofdeck | Roofdeck/Hotel DOAS Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0158 | PNL-DOAS-RD | DOAS-RD.2 (Network) | DOAS Unit | DOAS - Hotel/Roofdeck | Roofdeck/Hotel DOAS Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0159 | PNL-AHU-L2 | AHU-2M.1 (Network) | AHU (Modulating CHW-served) | AHU - Casino | 2nd Level/Casino MVAC Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0160 | PNL-AHU-L2 | AHU-2M.2 (Network) | AHU (Modulating CHW-served) | AHU - Casino | 2nd Level/Casino MVAC Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0161 | PNL-PAHU-RD | PAHU-RD.1 (Network) | Precooled Air Handling Unit | PAHU - Roofdeck | Roofdeck/PAHU Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0162 | PNL-PAHU-RD | PAHU-RD.2 (Network) | Precooled Air Handling Unit | PAHU - Roofdeck | Roofdeck/PAHU Plant | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0163 | PNL-EE-MAIN | MTR-MAIN-1 (Network) | Multifunction Power Meter (Main) | Power Metering | Main Switchgear Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0164 | PNL-EE-MAIN | MTR-MAIN-2 (Network) | Multifunction Power Meter (Main) | Power Metering | Main Switchgear Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0165 | PNL-EE-MAIN | MTR-MAIN-3 (Network) | Multifunction Power Meter (Main) | Power Metering | Main Switchgear Room | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0166 | PNL-EE-DIST | MTR-FDR-01 (Network) | Multifunction Power Meter (Feeder) | Power Metering | Distribution (per A4) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0167 | PNL-EE-DIST | MTR-FDR-02 (Network) | Multifunction Power Meter (Feeder) | Power Metering | Distribution (per A4) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0168 | PNL-EE-DIST | MTR-FDR-03 (Network) | Multifunction Power Meter (Feeder) | Power Metering | Distribution (per A4) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0169 | PNL-EE-DIST | MTR-FDR-04 (Network) | Multifunction Power Meter (Feeder) | Power Metering | Distribution (per A4) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0170 | PNL-EE-DIST | MTR-FDR-05 (Network) | Multifunction Power Meter (Feeder) | Power Metering | Distribution (per A4) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0171 | PNL-EE-DIST | MTR-FDR-06 (Network) | Multifunction Power Meter (Feeder) | Power Metering | Distribution (per A4) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0172 | PNL-EE-DIST | MTR-FDR-07 (Network) | Multifunction Power Meter (Feeder) | Power Metering | Distribution (per A4) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0173 | PNL-EE-DIST | MTR-FDR-08 (Network) | Multifunction Power Meter (Feeder) | Power Metering | Distribution (per A4) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0174 | PNL-EE-DIST | MTR-FDR-09 (Network) | Multifunction Power Meter (Feeder) | Power Metering | Distribution (per A4) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)
C0175 | PNL-EE-DIST | MTR-FDR-10 (Network) | Multifunction Power Meter (Feeder) | Power Metering | Distribution (per A4) | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) | 4P (8 wires) | Cat6 patch + permanent link | 30 | 1 | BACnet/IP or Modbus TCP — Cat6 to equipment controller; length 30 m (legacy_fallback)

## Trunks
ID | From | To | Cable Type | Length (m) | Notes
T0176 | BMS Server Room (head-end) | All BMS panels at 2nd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for 2nd Floor — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0177 | BMS Server Room (head-end) | All BMS panels at 3rd Floor | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for 3rd Floor — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0178 | BMS Server Room (head-end) | All BMS panels at Basement | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Basement — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0179 | BMS Server Room (head-end) | All BMS panels at Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Ground — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0180 | BMS Server Room (head-end) | All BMS panels at Lower Ground | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Lower Ground — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0181 | BMS Server Room (head-end) | All BMS panels at Roofdeck | Cat6 4P × 23 AWG U/UTP, FRLS jacket (BACnet/IP) — riser fiber + Cat6 trunk | 80 | Network trunk for Roofdeck — fiber to floor switch + Cat6 distribution to floor's BMS panels
T0182 | BMS Server Room (head-end) | All BMS panel controllers (MS/TP daisy-chain or branched) | BACnet MS/TP shielded twisted-pair trunk, 1pr × 22 AWG low-cap | 540 | MS/TP backbone interconnecting 18 BMS panels — refine after Q-008 layout review

## Panel Power Feeds
ID | From | To | Cable Type | Length (m) | Notes
P0183 | Local panelboard / EE-supplied feeder | PNL-AHU-L2 — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0184 | Local panelboard / EE-supplied feeder | PNL-BL-LZ — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0185 | Local panelboard / EE-supplied feeder | PNL-CH-PLANT-GND — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0186 | Local panelboard / EE-supplied feeder | PNL-CHWP-GND — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0187 | Local panelboard / EE-supplied feeder | PNL-CHWP-L2 — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0188 | Local panelboard / EE-supplied feeder | PNL-CT-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0189 | Local panelboard / EE-supplied feeder | PNL-DOAS-L2 — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0190 | Local panelboard / EE-supplied feeder | PNL-DOAS-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0191 | Local panelboard / EE-supplied feeder | PNL-EE-DIST — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0192 | Local panelboard / EE-supplied feeder | PNL-EE-MAIN — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0193 | Local panelboard / EE-supplied feeder | PNL-PAHU-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0194 | Local panelboard / EE-supplied feeder | PNL-PL-HZ — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0195 | Local panelboard / EE-supplied feeder | PNL-PL-LZ — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0196 | Local panelboard / EE-supplied feeder | PNL-VENT-BSMT — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0197 | Local panelboard / EE-supplied feeder | PNL-VENT-GF — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0198 | Local panelboard / EE-supplied feeder | PNL-VENT-L2 — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0199 | Local panelboard / EE-supplied feeder | PNL-VENT-L3 — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)
P0200 | Local panelboard / EE-supplied feeder | PNL-VENT-RD — BMS panel 240V power feed | 3C × 2.5 mm² FRLS (240V single-phase BMS panel power feed) | 30 | 240V single-phase 16A circuit to BMS panel; UPS-backed where in scope (A7); length 30 m (legacy_fallback)