## Summary
A4 — Panel Schedule Summary
Total panels | 18
Total physical I/O | 523
Total HLI subpoints | 166
Total network drops | 27
Total I/O points | 716
Estimated total controllers | 30
Estimated total power (W) | 885

## Panel Schedule
Panel | Location | System Scope | Equipment Count | Physical I/O | HLI Subpoints | Network Drops | Total I/O | DDC Controllers | Network Gateway | Total Controllers | Power (W) | Enclosure
PNL-AHU-L2 | 2nd Level/Casino MVAC Plant | AHU - Casino, AHU - Casino (Ozonizer) | 4 | 32 | 4 | 2 | 38 | 1 | 1 | 2 | 60 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-BL-LZ | Lower Ground/Boiler Room | Boiler/Laundry | 2 | 32 | 0 | 0 | 32 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-CH-PLANT-GND | GND/Chiller Plant Room | Chilled Water | 3 | 27 | 54 | 3 | 84 | 1 | 1 | 2 | 65 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-CHWP-GND | GND/BOH AHU Area | BOH Air Handling | 3 | 42 | 6 | 3 | 51 | 2 | 1 | 2 | 65 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-CHWP-L2 | 2F/CHW Pump Room | Chilled Water | 11 | 40 | 3 | 1 | 44 | 1 | 1 | 2 | 55 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-CT-RD | Roofdeck/Cooling Tower Area | Chilled Water | 6 | 31 | 0 | 0 | 31 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-DOAS-L2 | 2nd Level/Casino MVAC Plant | DOAS - Casino MVAC | 1 | 21 | 4 | 1 | 26 | 1 | 1 | 2 | 55 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-DOAS-RD | Roofdeck/Hotel DOAS Plant | DOAS - Hotel/Roofdeck | 2 | 42 | 8 | 2 | 52 | 2 | 1 | 2 | 60 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-EE-DIST | Distribution (per A4) | Power Metering | 10 | 0 | 50 | 10 | 60 | 1 | 1 | 2 | 100 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-EE-MAIN | Main Switchgear Room | Power Metering | 3 | 0 | 15 | 3 | 18 | 1 | 1 | 2 | 65 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-PAHU-RD | Roofdeck/PAHU Plant | PAHU - Roofdeck | 2 | 22 | 4 | 2 | 28 | 1 | 1 | 2 | 60 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-PL-HZ | Roofdeck/HW Plant | Plumbing & Sanitary Hotwater | 10 | 6 | 18 | 0 | 24 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-PL-LZ | Lower Ground/HW Plant | Plumbing & Sanitary Hotwater | 10 | 24 | 0 | 0 | 24 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-VENT-BSMT | Basement | General Ventilation | 16 | 48 | 0 | 0 | 48 | 2 | 0 | 2 | 50 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-VENT-GF | GF Main Lobby | General Ventilation | 9 | 27 | 0 | 0 | 27 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-VENT-L2 | 2nd Floor | General Ventilation | 13 | 39 | 0 | 0 | 39 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-VENT-L3 | 3rd Amenity & Guestroom | General Ventilation | 27 | 81 | 0 | 0 | 81 | 3 | 0 | 3 | 75 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare
PNL-VENT-RD | Roofdeck | General Ventilation | 3 | 9 | 0 | 0 | 9 | 1 | 0 | 1 | 25 | Wall-mount IP54 metal cabinet, sized per controller count + 30% spare

## Equipment per Panel
Panel | Equipment Instance
PNL-AHU-L2 | AHU-2M.1
PNL-AHU-L2 | AHU-2M.2
PNL-AHU-L2 | OZ-2M.1
PNL-AHU-L2 | OZ-2M.2
PNL-BL-LZ | SB-1
PNL-BL-LZ | SB-2
PNL-CH-PLANT-GND | CH-1
PNL-CH-PLANT-GND | CH-2
PNL-CH-PLANT-GND | CH-3
PNL-CHWP-GND | CHWP-1.1
PNL-CHWP-GND | CHWP-1.2
PNL-CHWP-GND | CHWP-1.3
PNL-CHWP-L2 | BTU-CHWS-MAIN
PNL-CHWP-L2 | COMP-1
PNL-CHWP-L2 | COMP-2
PNL-CHWP-L2 | COMP-3
PNL-CHWP-L2 | HDR-CHW-BP
PNL-CHWP-L2 | HDR-CHWR
PNL-CHWP-L2 | HDR-CHWS
PNL-CHWP-L2 | PCHWP-1
PNL-CHWP-L2 | PCHWP-2
PNL-CHWP-L2 | PCHWP-3
PNL-CHWP-L2 | PCHWP-4
PNL-CT-RD | CT-1
PNL-CT-RD | CT-2
PNL-CT-RD | CT-3
PNL-CT-RD | CT-COMMON
PNL-CT-RD | HDR-CWR-RD
PNL-CT-RD | HDR-CWS-RD
PNL-DOAS-L2 | DOAS-2W
PNL-DOAS-RD | DOAS-RD.1
PNL-DOAS-RD | DOAS-RD.2
PNL-EE-DIST | MTR-FDR-01
PNL-EE-DIST | MTR-FDR-02
PNL-EE-DIST | MTR-FDR-03
PNL-EE-DIST | MTR-FDR-04
PNL-EE-DIST | MTR-FDR-05
PNL-EE-DIST | MTR-FDR-06
PNL-EE-DIST | MTR-FDR-07
PNL-EE-DIST | MTR-FDR-08
PNL-EE-DIST | MTR-FDR-09
PNL-EE-DIST | MTR-FDR-10
PNL-EE-MAIN | MTR-MAIN-1
PNL-EE-MAIN | MTR-MAIN-2
PNL-EE-MAIN | MTR-MAIN-3
PNL-PAHU-RD | PAHU-RD.1
PNL-PAHU-RD | PAHU-RD.2
PNL-PL-HZ | HDR-HW-HZ
PNL-PL-HZ | HP-HZ-1
PNL-PL-HZ | HP-HZ-2
PNL-PL-HZ | HP-HZ-3
PNL-PL-HZ | HWT-HZ-1
PNL-PL-HZ | HWT-HZ-2
PNL-PL-HZ | HWT-HZ-3
PNL-PL-HZ | RP-HZ-1
PNL-PL-HZ | RP-HZ-2
PNL-PL-HZ | RP-HZ-3
PNL-PL-LZ | HDR-HW-LZ
PNL-PL-LZ | HP-LZ-1
PNL-PL-LZ | HP-LZ-2
PNL-PL-LZ | HP-LZ-3
PNL-PL-LZ | HWT-LZ-1
PNL-PL-LZ | HWT-LZ-2
PNL-PL-LZ | HWT-LZ-3
PNL-PL-LZ | RP-LZ-1
PNL-PL-LZ | RP-LZ-2
PNL-PL-LZ | RP-LZ-3
PNL-VENT-BSMT | EF-3SF.2
PNL-VENT-BSMT | EF-8R.1
PNL-VENT-BSMT | EF-B.1
PNL-VENT-BSMT | EF-B.2
PNL-VENT-BSMT | EF-BS.1
PNL-VENT-BSMT | EF-BS.2
PNL-VENT-BSMT | EF-GLZ.1
PNL-VENT-BSMT | EF-GLZ.2
PNL-VENT-BSMT | EF-HP.1
PNL-VENT-BSMT | EF-MC.1
PNL-VENT-BSMT | EF-MFP.1
PNL-VENT-BSMT | EF-PR.1
PNL-VENT-BSMT | EF-PR.2
PNL-VENT-BSMT | EF-RR.2
PNL-VENT-BSMT | TEF-B.1
PNL-VENT-BSMT | TEF-B.2
PNL-VENT-GF | EF-1.2A
PNL-VENT-GF | EF-1MR.1
PNL-VENT-GF | EF-1ST0.1
PNL-VENT-GF | EF-LPG.1
PNL-VENT-GF | EF-MRF.1
PNL-VENT-GF | TEF-1.1
PNL-VENT-GF | TEF-1.2
PNL-VENT-GF | TEF-1.3
PNL-VENT-GF | TEF-1.4
PNL-VENT-L2 | EF-2.1
PNL-VENT-L2 | EF-2.2
PNL-VENT-L2 | EF-2.3
PNL-VENT-L2 | EF-2.4
PNL-VENT-L2 | EF-2B.1
PNL-VENT-L2 | EF-2B.2
PNL-VENT-L2 | EF-CHR.1
PNL-VENT-L2 | EF-CHR.2
PNL-VENT-L2 | EF-GS.1
PNL-VENT-L2 | EF-GS.2
PNL-VENT-L2 | TEF-2.1
PNL-VENT-L2 | TEF-2.3
PNL-VENT-L2 | TEF-2B.3
PNL-VENT-L3 | EF-3.1
PNL-VENT-L3 | EF-3.2
PNL-VENT-L3 | TEF-3A.1
PNL-VENT-L3 | TEF-3A.2
PNL-VENT-L3 | TEF-3B
PNL-VENT-L3 | TEF-3C.1
PNL-VENT-L3 | TEF-3C.2
PNL-VENT-L3 | TEF-3D.1
PNL-VENT-L3 | TEF-3D.10
PNL-VENT-L3 | TEF-3D.11
PNL-VENT-L3 | TEF-3D.12
PNL-VENT-L3 | TEF-3D.13
PNL-VENT-L3 | TEF-3D.14
PNL-VENT-L3 | TEF-3D.15
PNL-VENT-L3 | TEF-3D.16
PNL-VENT-L3 | TEF-3D.17
PNL-VENT-L3 | TEF-3D.18
PNL-VENT-L3 | TEF-3D.19
PNL-VENT-L3 | TEF-3D.2
PNL-VENT-L3 | TEF-3D.20
PNL-VENT-L3 | TEF-3D.3
PNL-VENT-L3 | TEF-3D.4
PNL-VENT-L3 | TEF-3D.5
PNL-VENT-L3 | TEF-3D.6
PNL-VENT-L3 | TEF-3D.7
PNL-VENT-L3 | TEF-3D.8
PNL-VENT-L3 | TEF-3D.9
PNL-VENT-RD | EF-1 (RD)
PNL-VENT-RD | EF-RD.1
PNL-VENT-RD | EF-RD.2